## Overview
Multizone to Variable Volume HVAC Controls Retrofit Scoping Guide
A. Objective
This Scoping Guide is intended to help assess multizone (MZ) air handling unit operational status and suitability for retrofit. The results of this scoping will inform a contract performance work statement for units selected for retrofit.
B. Scoping Process
The process consists of identifying, assessing, and selecting constant volume (CV) MZ systems suitable for conversion into more energy-efficient variable volume (VV) systems. The retrofit focuses primarily on the HVAC control system, with minimal equipment replacement or disruption of building functions during the retrofit.
The basic steps include:
1. Familiarization
Get familiar with the technology and retrofit. Review Technical Note; ‘Multizone to Variable Volume HVAC Controls Retrofit for Energy Efficiency’ included in '1.Familiarization' tab for your convenience. Skim 'Reference' tab in this worksheet. You may decide to use the 'MZ to VV Savings Estimator' spreadsheet tool to determine potential energy and cost impact. See the Whole Building Design Guide website, www.wbdg.org/ffc/army-coe/design-guides, for the savings estimator and other resources.
2. Installation Preliminary Scoping
a. Team up with DPW / OMD staff and create a first pass list of units along with their basic characteristics on the 'Installation Prelim Scoping' tab.
b. Locate, identify, and characterize (in a simplified big picture fashion) each multizone unit at the Installation.
c. For each unit, provide an initial recommendation on whether to perform a subsequent field inspection (yes, no, maybe).
d. Pick one or two strong candidates to start with, and work through the entire process before taking on all potential units. This gives you a chance to tailor additional data collection to your needs.
3. Preparation for Field Inspection | `
a. Document Gathering: For units pre-selected for potential ‘field inspection’ during the ‘Installation Prelim Scoping’ step above, obtain available documentation as listed below to determine MZ unit type and sizes; where the intent is to help prioritize units for field inspection because they are good retrofit candidates; e.g. conventional MZ units that are large, have big motors, large cfm, large sf served, serve conference rooms, classrooms, or other spaces with highly variable occupancy.
Documents may include:
i. Mechanical As-Built Construction (or design) Drawings/Documents (High Priority Item, Schedules are key)
ii. Equipment List
iii. AHU Data Sheet
iv. TAB Report
v. Control Drawings
vi. Any individual energy meter data
vii. Any previous mechanical audits
b. Equip Tables & Field Data: Pre-Fill the forms under the ‘Equip Tables & Field Data’ tab using the available documentation and the ‘Installation Prelim Scoping’ results.
c. DPW-Maint Staff Interviews: Duplicate the information in the 'DPW-Maint Staff interviews' tab for each unit identified for possible field inspection in 'Installation Prelim Scoping'. Answer the questions in coordination with DPW/techs/maintenance staff for each unit. This may be more or different people from the installation preliminary scoping.
d. Second round prioritization: Update priority of units on 'Installation Prelim Scoping' tab for detailed field inspection based on gathered documents and interviews.
e. Copy ‘Detailed Field Inspection’: Make multiple copies of the ‘Detailed Field Inspection’ tab, one for each unit with enough promise for retrofit to merit a field inspection. Rename the new spreadsheet tabs to uniquely ID each MZ unit.
f. Tool Bag. Gather basic tools for a Field Inspection:
i. Survey Forms on clipboard or computer/tablet
ii. Camera
iii. Flashlight
iv. 10' step ladder
v. Screwdriver
vi. Wrench
4. Field Inspection
a. Visit building(s) with DPW / maintenance staff to 1) complete the forms, 2) guide a decision to retrofit or not, and 3) to document needed repairs to include in a potential retrofit scope of work.
b. Populate ‘Equip Tables & Field Data' sheet with nameplate data.
c. Work through the ‘Detailed Field Inspection' data sheet to ID suitability for an Air Flow Measurement Station and any 'additional' work beneficial to the unit/system. Complete ‘Equip Tables & Field Data' sheet.
d. Log pertinent observations and take photos of key aspects and components.
5. Post Field Inspection (Not covered in this workbook)
The objective at this stage is to decide if it is feasible and reasonable to pursue a retrofit.
a. Organize and distill site visit data.
b. Perform economic calculations as applicable.
c. Prioritize candidate units and select/recommend units (if any) for retrofit.
6. Design/Specification (Not covered in this workbook)
For units selected/approved for retrofit, create scope of work, specifications and drawings.

## 1. Familiarization
1 | Review Multizone to Variable Volume HVAC Controls Retrofit for Energy Efficiency Technical Note for a technology overview, field demonstration results and application insights.
This is an eight page document, DOUBLE CLICK to open.
This is the Technical Note as of April 2022. Any document updates are posted on the Whole Building Design Guide, www.wbdg.org/ffc/army-coe/design-guides

## 2. Installation Prelim Scoping
Purpose: Identify candidate multizone units for controls retrofit that merit further consideration and possible field inspection.
* Consider cfm, motor size, sf served (e.g. Small: SF < 5hp or CFM < 3000; Medium: 5hp < SF < 15hp or 3000 < cfm < 10000; Large: SF > 15hp or cfm > 10,000) ** Fair to good condition, or poor but fixable at reasonable cost. No building remodel/ decommission planned *** Assign priority to all units where highest priority is for large, Conventional MZs (Hot deck/Cold Deck) that serve spaces w/ high variability in occupancy (conference rooms, classrooms) w/ 10yrs life left. Get maintenance staff input and recommendations.
Complete information as available:
| Bldg Name/ Number | Unit ID# and/ or location | MZ Type (Conv, Bypass, Neutral) | Approx. Age (yrs) | Approx. Unit Size* (Small, Medium, Large) | 10 yrs service left? ** | Notes (known condition, repair needs, issues, reason < 10 yrs life left) | Controls (DDC , Analog Electronic, Pneum.) | Controls Vendor | LON/ BACNet/Niagara/Other | Initial Recommendation to Field Inspect? (Y/N, Maybe) | Priority*** (High, Medium, Low)
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24

## 3b. Equip Tables & Field Data
Equip Tables & Field Data | [20 empty] | Equip Tables & Field Data | [12 empty] | Equip Tables & Field Data | [11 empty] | Equip Tables & Field Data
Bldg Name/ Number | Unit ID# and/ or location | AHU Information |  | Fan Motor Information | [16 empty] | Zone Information | [12 empty] | Heating and Cooling Coil Information | [11 empty] | Chiller/ AC Information |  |  |  | Boiler(s)/ Burner Information |  |  |  | Seasonal Deck Operation
|  | MZ Type (Conv, Bypass, Neutral) | Approx. Age (yrs) | Supply Fan CFM | Supply Fan Motor | [6 empty] | RA | Return or Exhaust Fan Motor | [7 empty] | Total Area Served (SF) | Number of Zones | Variable occupancy spaces… Approximate portion of 'Total Area Served' (SF) by end use (%) | [10 empty] | Cooling Coil |  |  |  | Main Unit Heating Coil |  |  |  | Zone Duct Heating Coil |  |  |  | Location | Make/Model | Capacity (Btu/hr) | Efficiency (COP) | Location | Make/Model | Capacity (Btu/hr) | Efficiency (%) | Winter |  | Spring/Fall |  | Summer
[5 empty] | Mfg. | Model/ Part Number | HP | Eff. | Voltage | Date/ Age | OK for VFD? | Plenum or ducted return air? | Mfg. | Model/Part Number | HP | Eff. | Voltage | Date/ Age | OK for VFD ? | Air Side Economizer? (Y/N) |  |  | Classroom (%) | Conference / Assembly (%) | Rest Room (%) | Gym (%) | Shop (%) | other (%) | other (specify) | Observed Balancing Damper (%Open) Position | Scheduling Eqpt? (mechanical time clock, electronic time clock, BAS, none) | Is unit currently running 24/7? | Is 24/7 operation needed? | Cooling Type (ChW, Dir Expn) | Capacity (Btu/hr) | Valve Make/Model | Condition Assessment | Heating Type (HW, NG) | Capacity (Btu/hr) | Valve Make/Model | Condition Assessment | Heating Type (HW, NG) | Capacity (Btu/hr) | Valve Make/Model | Condition Assessment | [8 empty] | HD, CD, or Both | Boiler/ Chiller Operation | HD, CD, or Both | Boiler/ Chiller Operation | HD, CD, or Both | Boiler/ Chiller Operation

## 3c. DPW-Maint Staff Interview
3 | MZ Unit __________________________ Date_________________________
a. | Known issues with the AHU and the spaces it conditions. Examples include fan operational issues (too loud, vibrates, etc.), valve/damper issues, duct/coil/damper/AHU floor corrosion/microbial growth, space conditioning capacity or accuracy, repeated complaints. Note below:
b. | What is the general condition of the HVAC mechanicals? What needs to be fixed? Be open to improving and fixing any existing problems as a part of the retrofit. Does this unit have 10 yrs of life in it? Can needed repairs be made at a reasonable cost? Note below:
c. | Existing controls system connectivity status. Is local HVAC connected to a central Utility Monitoring Control System (UMCS)? Is there ability to log into a local Building Automation System (BAS) to look at the AHU operations?
Note Below:
d. | What is the general Control System condition? What needs to be fixed? Are there actuator control issues or sensor readings clearly out of range? Be open to improving and fixing any existing problems as a part of the retrofit. Note below:
e. | Are there issues with the current zoning? Has the end use of a space changed since the system was installed which presents problems? Is there a "dominant" zone that is always calling for full heating or cooling? What other information can they tell you about the zones? An example is occupants are always hot/cold. Note below:
f. | Discuss the sequence of operations and schedule of the unit: If there is an economizer, how is it controlled? Hot-Deck/Cold-Deck Temperature Reset strategy? Is there a seasonal deck shutoff? Note below:

## 3d. Detailed Field Inspection
Detailed Field Inspection (with HVAC and Controls Technician)
3d | MZ Unit __________________________ Date_________________________
Intent: Determine the operational condition of the AHU to guide a decision to retrofit or not, and to document needed repairs to include in a potential retrofit scope of work. Identify issues such as leaking valves/dampers/ducts, severe corrosion, or any other malfunctioning equipment that would reduce energy savings and cause O&M challenges. Some equipment may be too challenging to access/explore; make note of inaccessible equipment. Take many pictures of the equipment and their nameplates for future reference.
a | Compare the mechanical as-builts, equipment list, AHU data sheet with the existing unit
Some specific things to note:
Is there an air side economizer? Verify with a Controls Technician. Check drawings, controls programming. (Economizer control uses outside air for "free cooling" in mild weather. Although an economizer requires an an OA Temp sensor, and a actuator linked to the OA and RA damper, their presence is not sufficient to determine existence of economizer control.)
|  | Yes |  |  | No
Is there preheat on the AHU? This is a heating coil located before a cooling coil to prevent freezing.
|  | Yes |  |  | No
Note any other significant differences between the unit and the documents, mark up and note below:
3d | MZ Unit __________________________ Date_________________________
b | Locate and inspect the Outside Air intake for suitability to add an Air Flow Measurement Station (AFMS).
Adding a AFMS will ensure adequate ventilation for the building. An AFMS requires a certain distance of unobstructed flow up and downstream of the station for proper measurement. Typically requirements are two' Duct Diameters' (distance) upstream of the flow station, one 'Duct Diameter' downstream. However this requirement is dependent on the flow station type and manufacturer.
-Take pictures of the OA ducting for reference.
-What is the available length (distance) in the OA duct to install an AFMS? Specifically; determine the straight-duct distance between duct disturbances (obstructions) such as the intake louver/hood and a downstream damper. Other obstructions might include a duct elbow or tee.
| OA Duct Distance between duct disturbances: | [6 empty] | feet
What is the diameter of the OA duct? For a rectangular duct, calculate 'equivalent' diameter:
Duct Dimensions: |  | Height = |  | inches |  | Width = |  | inches
Duct Diameter (Equivalent) = |  |  | (W + H) |  | Duct Diameter = |  |  | inches
2
c | Look for and note damage on the ducting or equipment that appears significant enough to warrant repair. (Damage that would hinder AHU operation would hurt the ability of the AHU to condition the space properly and prevent energy savings)
This includes corrosion (ducts, dampers, heating/cooling coils, drain pan, motor mounts, etc.), broken or damaged ductwork (e.g. split seams), loose, degraded or missing AHU or duct insulation, flex ducts not connected to diffusers, flex ducts that are flattened or distorted:
d | Review drawings to inspect the Outside Air, Supply Air, and Return Air ducting path. Does the ductwork run through any unconditioned spaces for a distance over 50 feet? (If so, insulation or duct leakage may be a concern.)
|  | Yes |  |  | No
3d | MZ Unit __________________________ Date_________________________
e | Inspect AHU dampers. Look for operational issues on accessible dampers such as seals falling off that prevent full closing, bent or damaged blades, excessive play in the dampers (not tight on shaft), loose set screws/linkages. Note issues below.
Issues:
OA Damper
RA Damper
EA Damper
Zone Damper 1
Zone Damper 2
Zone Damper 3
Zone Damper 4
Zone Damper 5
Zone Damper 6
Zone Damper 7
Zone Damper 8
3d | MZ Unit __________________________ Date_________________________
f | Test the AHU valves and dampers ability to fully actuate from open to close. (If valves or dampers cannot fully stroke from open to close the AHU cannot operate as needed, and would need repair)
Valves: Fully actuate all valves using the BAS/DDC or manual override. Can the valves fully stroke from open to close?
Verify with the HVAC technician. Actuators may have a position indicator on the actuator but may be difficult to read. There also may be no position indicator.
|  | Yes | No | Issues:
CC Valve
HC Valve
Preheat Valve
Zone Valve 1
Zone Valve 2
Zone Valve 3
Zone Valve 4
Zone Valve 5
Zone Valve 6
Zone Valve 7
Zone Valve 8
Dampers: Fully actuate all dampers using the BAS/DDC or manual override
Verify with the HVAC technician. Actuators have a position indicator on the actuator but may be difficult to read or is not there. Dampers may also potentially be observed with AHU door open.
Dampers include the zone dampers, mixed air damper assembly (linked OA, RA EA).
Can the dampers fully actuate from open to close?
|  | OA Damper | RA Damper | Zone Damper 1 | Zone Damper 2 | Zone Damper 3 | Zone Damper 4 | Zone Damper 5
Yes
No
Issues observed
|  | Zone Damper 6 | Zone Damper 7 | Zone Damper 8 | Zone Damper 9
Yes
No
Issues observed
3d | MZ Unit __________________________ Date_________________________
g | Test to see if any valves are leaking (Leaking valves either heat or cool the air when it is not required, reducing comfort and energy savings)
Close the valves and ensure they are fully closed by verifying on the actuator
Ensure the heating (or cooling) is on by using the Building Automation System.
Watch temperature sensors either on the unit or on the control system
Does the temperature go up (heating) or down (cooling)?
|  |  | CC Valve | HC Valve | Duct HC Valve
Yes
No
Perform a visual inspection on the valve for any external leakage to determine if repair is needed. Is there visible external damage?
|  |  | CC Valve | HC Valve | Duct HC Valve
Yes
No
h | Visually Inspect the Freeze Stat
1 | Is it serpentined across the duct up-and-down or side-to-side? (Up and down could lead to false tripping and incorrect operation.)
| Up-and-Down |  |  |  | Side-to-Side
2 | Is there visible damage or clear sign the stat is old or original?
|  | Yes |  |  | No
i | Inspect the temperature sensors and answer the question below
Are Hot-Deck and Cold-Deck temperature sensors single point or averaging type?
[5 empty] | Hot-Deck | Cold-Deck
Averaging or Point Sensor?
What would it take to access the sensor in case they need to be changed out with the retrofit? Describe below.
3d | MZ Unit __________________________ Date_________________________
j | Check for unsatisfied zones
Ask the service technician if there is an "unsatisfied" zone that is always calling for full heating or full cooling. An unsatisfied zone may be able to be remedied with TAB and commissioning, but may not. If needed, trending of space temperatures would show if setpoint is reached. If there is no time when all zones are satisfied, the controls upgrade will not save energy and should be dropped from consideration for this unit.
Is there an unsatisfied zone ?
|  | Yes |  |  | No
If so, either recommend TAB or drop this unit.
k | Review the control system graphics and schedules, if possible
Inspect the graphics to ensure they are accurate compared to the equipment setup. For example, if the AHU has a preheat coil, does it appear on the graphics? (Accurate graphics allow for proper operations and maintenance).
Review the AHU schedule, compare it to the building occupation schedule
Review the seasonal shutoff, does the hot deck shut off in the summer and cold deck shut off in the winter?
|  |  | Accurate Graphics | Accurate Schedule | Seasonal Shutoff
Yes
No
Make note of any other concerns or issues found in the graphic review, such as any equipment or points overridden: