Fire Protection / Life Safety / Accessibility Code Review

Template version 1 dated [X XXX XXXX]

Applicability: In accordance with Unified Facilities Criteria (UFC) 3-600-01, a fire protection, life safety and accessibility code review shall be developed and included in all project submittals for government review and comment, including unoccupied facilities. Fire protection, life safety and accessibility floor plan(s) drawings shall be developed and included in all project submittals for government review and comment. Instructions: The designer of record (DOR) shall use this form to record fire protection, life safety and accessibility features for all building projects, including unoccupied facilities. The form shall be edited. Provide a separate form for each building on the project. This code review form is not a substitute for a detailed fire protection/life safety/accessibility code analysis per UFC 3-600-01. This includes the addition of criteria/standards followed on the left with actual method to meet criteria on the right. The information on the right are the minimum requirements and DOR is required to provide all the information as indicated below. The DOR must also sign the form where indicated. The signed form shall be provided in the Design Analysis and same review text shall be included on a code review drawing. Fire protection, life safety and accessibility drawings shall be developed, graphically showing all features of fire protection/ life safety/accessibility in plan. These drawings shall include note, "This drawing is for reference only. It is not part of the construction contract, and all information contained here is located on construction documents". In accordance with UFC 3-600-01, drawings shall illustrate features from all disciplines including longest travel distance, longest dead-end distance, longest common path, accessible means of egress, wall ratings, emergency lights, exit signs, manual alarm pulls, detectors, strobes, speakers, horns, fire alarm control panel (FACP), and fire extinguishers. This fire protection, life safety, and accessibility code review worksheet is only a portion of the required life safety documentation. Projects that meet the definition of "major project" shall comply with UFC 3-600-01. Provide submittals in accordance with Engineering Regulation (ER) 1110-345-700: QFPE signed and stamped code compliance site plan. QFPE signed and sealed final design analysis and life safety plans. Compliance letter signed and stamped by the QFPE at final or corrected final Waiver/Exemption: For all waivers and exemptions to the DoD Building Code for which the Army is a project sponsor or landholder, the building official/authority having jurisdiction (BO/AHJ) must obtain approval from the Army Engineering Senior Executive Panel (ESEP) member, HQUSACE Director of Engineering and Construction. [The blue bracketed, and/or italicized text is provided for informational purposes and should be updated and/or deleted in the final document.]

| [Project Name, P2 or PN and Location] |  |  |
| --- | --- | --- |
| 1. APPLIED CODES AND STANDARDS |  |  |
| [Edit codes and dates listed below to indicate the applicable dates and change number for any codes and standards used for this project.] |  |  |
| CODE TITLE |  | VERSION |
| - UFC 1-200-01 DoD Building Code |  | [Change 4, 17 Dec 2024] |
| - UFC 3-600-01 Design: Fire Protection Engineering for Facilities |  | [Change 1, January 2010] |
| - UFC 4-021-01 Design and O&M: Mass Notification Systems |  | [Change 6, 6 May 2021] |
| - International Building Code (IBC) |  | [2024] |
| - NFPA 1 Fire Code |  | [2024] |
| - NFPA 101 Life Safety Code |  | [2024] |
| - NFPA 10 Standard for Portable Fire Extinguishers |  | [2022] |
| - NFPA 13 Standard for Installation of Sprinkler Systems |  | [2025] |
| - NFPA 20 Standard for the Installation of Stationary Pumps for Fire Protection |  | [2022] |
| - NFPA 22 Standard for Water Tanks for Private Fire Protection |  | [2023] |
| - NFPA 30 Flammable and Combustible Liquids Code |  | [2024] |
| - NFPA 30A Code for Motor Fuel Dispensing Facilities and Repair Garages |  | [2024] |
| - NFPA 70 National Electrical Code (NEC) - Article 500 Hazardous Locations & Article 511 Commercial Garages, Repair & Storage |  | [2023] |
| - NFPA 80 Standard for Fire Doors and Other Opening Protectives |  | [2025] |
| - NFPA 72 National Fire Alarm and Signaling Code |  | [2025] |
| - NFPA 291 Recommended Practice for Fire Flow Testing and Marking of Hydrants |  | [2025] |
| - NFPA 400 Hazardous Material Code |  | [2025] |
| - ASME A17.1 Safety Code for Elevators and Escalators |  | [2021] |
| - ABA (Architectural Barriers Act) Accessibility Standards, as directed by DoD Policy Memo "Access for People with Disabilities" |  | [dated 31 Oct 2008] |
| - ECB 2018-17, New Requirements for Visual Notification for Mass Notification Systems |  | [issued 26 Mar 2025 - expires 26 Mar 2027] |
| 2. BUILDING CODE REQUIREMENTS: |  |  |
| - Occupancy Classification: |  |  |
| - IBC Chapter 3 | [Indicate project's occupancy classification information based on IBC for building code requirements.] |  |
| - Construction Type: |  |  |
| IBC Chapter 6 Table 601 | [Indicate project's building code (IBC) construction type.] |  |
| - Mixed Use & Occupancy Separations |  |  |
| UFC 3-600-01 [par. 5-4, 5-5] IBC Section 508 | [Indicate project's intention for mixed use or separated occupancy. Per UFC 3-600-01: 5-5, IBC Section 509 does not apply. Include equations proving the area allowances for separated occupancy per 508.4.2 if it applies. For example: S-1 H-2 22,300 SF + 213 SF = .347 < 1 (OK) 65,625 SF 26,250 SF ] |  |
| - Area Limitations / Modifications: |  |  |
| UFC 3-600-01 [par. 5-3] IBC Section 503, 506, 507 | [Indicate project's area limitations, Table 506.2. Describe area modifications taken. Include equations proving allowable area increases using frontage and automatic sprinkler factors. Only need to show increases if needed to increase allowable area. For example: Area determination: At = 16000 > actual = 9503 Is = 2 for sprinkler increase If = 0 Aa = 16000 + [16000(0)] + [16000(2)]= 48000 > actual 27843 (OK)] |  |
| - Height Limitations: |  |  |
| IBC Section 503 Tables 504.3 and 504.4 | [Indicate specific project's height limitations, providing maximum height allowed and actual height per building height definition in Section 502.] |  |
| - Vertical Enclosures, Continuity, Protection: |  |  |
| UFC 3-600-01 [par. 3-3.1.1] NFPA 101: 7.1.3, 8.6, 8.7 NFPA 90A: 4.3.1.2, 5.3.4 | [Indicate fire protection provisions for stair enclosures, utility shafts, elevators, laundry chutes, etc. Indicate vertical enclosure requirements & provisions based on number of building stories for stairways, elevator hoistways, light shafts, building expansion joints, etc. List required fire resistance ratings of shafts, for example: 2-Story Shaft Enclosures - ( ) hour rating; 3-Story Laundry Chute Enclosure - ( ) hour rating.] |  |
| - Opening Protectives & Thru-Penetrations |  |  |
| NFPA 101: 8.3 thru 8.6 NFPA 90A NFPA 80 NFPA 13 | [Indicate requirements & provisions for fire barriers, smoke partitions, smoke barriers, vertical openings, and special hazard protection. Per NFPA 13, 8.15.4, vertical openings not meeting 8.15.4.4 require closely spaced sprinklers and draft stops.] |  |
| - Horizontal Separations: |  |  |
| IBC Table 508.4 | [Indicate location for horizontal separation and provision such as fire or smoke rated floors between occupancies or exit enclosures.] |  |
| - Fire Resistive Requirements: |  |  |
| IBC Table 601 and Section 602 | [Indicate requirements based on construction type, for example: Primary Structural Frame - ( ) hour rating Exterior Bearing Walls - ( ) hour rating Interior Bearing Walls - ( ) hour rating Exterior Nonbearing partitions - ( ) hour rating Interior Nonbearing partitions - ( ) hour rating Floor Construction & Secondary Members - ( ) hour rating Roof Construction & Secondary Members - ( ) hour rating ] |  |
| - Enclosure protection: |  |  |
| NFPA 101: Specific occupancy chapters ASME A17.1 | [Indicate enclosure protection requirement for specific spaces and what is provided in the design, for example: Mechanical Rm requires 1 Hr or sprinklered - sprinkler provided. Janitor Closet requires 1 Hr or sprinklered - Sprinkler provided. Elevator control room requires 1 Hr - 1 Hr provided.] |  |
| UFC 3-600-01 [par. 4-46.2] | [Indicate enclosure protection requirement for Recycle Room.] |  |
| UFC 3-600-01 [par. 4-48.5.2.2] | [Indicate fire barrier separation requirement between the warehouse and storage area from offices and shops area.] |  |
| NFPA 400 UFC 3-600-01 [par. 4-20] | [Indicate the Maximum Allowable Quantity (MAQ) for each type of hazardous material and the actual anticipated amount that will be stored. ] |  |
| - Protection from hazards: NFPA 101: 8.7 Special Hazard Protection NFPA 101: X.3.2 | [Indicate how the space(s) (general storage, boiler or furnace rooms, maintenance shops that include woodworking and painting areas) been protected. ] |  |
| - Fire Protection System: |  |  |
| UFC 3-600-01 [Chapters 4 & 9] | [Determine the requirement for fire protection systems, stating which systems are required and criteria to which they are designed.] |  |
| UFC 3-600-01 [Appendix B] | [Indicate the occupancy hazard category based on occupancy for various rooms, using UFC 3-600-01, Appendix "B". Consider classifying the entire building and noting exceptions for differing rooms. For example, for a light hazard (LH) building, the mechanical, electrical and storage rooms are classified as ordinary hazard (OH).] |  |
| UFC 3-600-01 [par. 9-7, except as modified in Chapter 4 of UFC for specific facility types] UFC 3-600-01 [par. 1-12.12, 9-7.3.1.2, 4-46] NFPA 13 | [For each occupancy hazard category based on Tables 9-3 & 9-4 for non-storage applications, indicate Sprinkler Design Density, Sprinkler Design Area, Water Demand for Hose Streams, providing supply pressure and source requirements.] [For warehouse and storage occupancy, indicate commodity classification; maximum potential storage height must be based on roof or ceiling height, storage configuration (racks, shelves, palletized, bin box, and solid-piled), aisle width, clearance to ceiling, and roof slope. Indicate design density, sprinkler design area, sprinkler type, K-factor, minimum operating pressure, and water demand for hose stream. ] |  |
| UFC 3-600-01 [Chapter 9-7.4] NFPA 13 | [Coverage per sprinkler must be in accordance with NFPA 13, not exceeding 225 sf for light hazard, 130 sf for ordinary hazard, or 100sf for extra hazard. Extended coverage heads are not permitted.] |  |
| - Available Water Supply Testing |  |  |
| UFC 3-600-01 [par. 1-12.5, 9-6.4] NFPA 291 | [Provide results of water flow tests per the UFC which requiring QFPE to direct the flow testing per NFPA 291. The flow test must have sufficient discharge to cause a drop in pressure at the residual hydrant of at least 10 percent. Water supply data shall show available water supply, static pressure, & residual pressure at flow. Based on this data & estimated flow & pressure required for the building sprinkler system(s), determine the need for a fire pump. Indicate test & flow hydrant locations, elevations, & water flow data on contract drawings.] |  |
| UFC 3-600-01 [par. 9-2.2] NFPA 1: Table 18.4.5.2.1 | [Indicate fire flow and duration requirement for sprinkler and non-sprinklered facilities.] |  |
| UFC 3-600-01 [par. 1-12.10, 4-40] | [For range and remote facilities, indicate the fire flow requirement per NFPA 1142. Provide information indicating how the local fire department will meet the fire flow requirement. Provide code analysis and calculation per NFPA 1142 to District Fire Protection Engineer (DFPE) to get AHJ concurrence.] |  |
| - Water Storage Tank Requirements |  |  |
| UFC 3-600-01 [par. 1-12.4, Chapter 9-4] NFPA 22 | [Indicate water storage requirements including capacity, type of storage tank and storage tank monitoring.] |  |
| - Backflow Preventer & Testing |  |  |
| NFPA 13: 8.16.4.6.1 UFC 3-600-01 [par. 9-6.3.5, 9-6.6] | [Provide backflow preventer valves as required by local authority or water surveyor. On contract drawings show and provide test piping and valve located downstream of the backflow preventer for flow testing of the backflow preventer at full system demand flow. Route the discharge to an appropriate location outside the building. Minimum pressure drop across reduced pressure backflow preventer is 12 psi and 8psi for double check backflow preventer. Assure that backflow preventer is 8 psi for hydraulic calculations for double check and 12 psi for reduce pressure.] |  |
| - Fire Pump(s) |  |  |
| UFC 3-600-01 [Chapter 9-5] NFPA 20 UFC 3-600-01 [par. 9-5.1.4] | [Provide information regarding project site reliable power. Provide fire pump(s) flow and pressure requirements, locations, construction enclosure, fire pump and fire pump controller maintenance access.] |  |
| 3. LIFE SAFETY REQUIREMENTS: |  |  |  |
| - Classification of Occupancy: |  |  |
| NFPA 101: Ch. 6 | [Indicate project's occupancy classification information based on NFPA 101 for life safety code requirements. Exception For Repair Garage, UFC 3-600-01: 4-43.1.2 to use NFPA 30A (3.3.12.2 & NFPA 101 40-1.2.1)] |  |
| - Occupant Load: |  |  |
| NFPA 101: 7.3.1.2 & Chapters 12-42 UFC 3-600-01 [par. 10-3.1] | [Indicate total occupant load, showing occupant load factors and subtotals of various occupancies for each floor, for example: Actual floor area Business: 5,626 GSF / 100 GSF = 56.37 ~ 57 Actual floor area Assembly: 1,920 NSF / 15 NSF = 128.002 ~ 129 Total Floor Maximum Occupancy: 186 Supplemental Occupant Load Factors found in UFC 3-600-01, para. 10-3.1, shall be included when calculating the total occupant load for the facility.] |  |
| - Capacity of Means of Egress: |  |  |
| NFPA 101: 7.3.3 & Chapters 12-42 | [Indicate egress capacity for components of all means of egress including stairs, corridors, ramps, and doors. Include total egress capacity needed.] |  |
| - Number of Exits: |  |  |
| NFPA 101: 7.4 & Chapters 12-42 | [Indicate number of exits required based on egress capacity needed. Indicate number of exits provided.] |  |
| - Arrangement of Means of Egress |  |  |
| NFPA 101: 7.5 & Chapters 12-42 | [Indicate requirements for means of egress arrangement, including project's provisions to comply.] |  |
| - Accessible Means of Egress |  |  |
| NFPA 101: 7.5.4 | [Indicate requirements for accessible means of egress with project's provisions to comply.] |  |
| - Travel Distance to Exits: |  |  |
| NFPA 101: 7.6 & Chapters 12-42 | [Indicate travel distance requirements and project's provisions to comply using worst case distance. Include common path, dead end, and travel distance limits for each occupancy.] |  |
| - Illumination of Means of Egress: |  |  |
| NFPA 101: 7.8 & Chapters 12-42 | [Indicate required and provided provisions for means of egress illumination.] |  |
| - Emergency Lighting: |  |  |
| NFPA 101: 7.9 & Chapters 12-42 | [Indicate required and provided provisions for emergency lighting.] |  |
| - Marking of Means of Egress: |  |  |
| NFPA 101: 7.10 & Chapters 12-42 | [Indicate required and provided provisions for marking of egress lighting.] |  |
| - Interior Finish Classification Limits: |  |  |
| NFPA 101: Table A.10.2.2 | [Indicate required and provided provisions for interior finish classification limitations.] |  |
| - Detection, Alarm, & Communications: |  |  |
| UFC 3-600-01 [Chapter 9-18] NFPA 101: 9.6 & Chapters 12-42 | [Indicate requirements for manual alarm initiation, automatic detection, and alarm notification. Include location to which notification is sent.] |  |
| - Portable Fire Extinguishers: |  |  |
| UFC 3-600-01 [par. 9-17] NFPA 10 | [Indicate requirements for FE and project provision. See provision in Draft AR DG Pamphlet, 3-4.1.5 for Arms Vaults.] |  |
| - Corridors: |  |  |
| NFPA 101: Chapters 12-42 | [Indicate requirement and provisions for corridor protection including any fire and smoke ratings and door ratings.] |  |
| - Fire Dampers: |  |  |
| NFPA 90A: 9.1 | [Fire dampers shall be dynamic type, rated for 3,000 ft./min or greater. Edit the following or insert other requirements for this project: Fire rated dampers shall be installed in ducts passing through partitions or walls having a fire resistance rating of 2 hours or greater. Fire dampers shall be installed in ducts passing through fire resistance rated shafts. Fire dampers shall be installed in air transfer openings in fire resistance rated partitions. Fire dampers shall be installed in ducts passing through floors except where the floor penetration is within a fire rated shaft.] |  |
| - Smoke Dampers: |  |  |
| NFPA 90A: 9.3 | [Indicate requirements & project's provision for dynamic smoke dampers. Provide isolation smoke damper when air handling equipment systems have a capacity greater than 15,000 cfm to isolate the air-handling equipment, including filters, from the remainder of the system on both the building supply and return sides, in order to restrict the circulation of smoke.] |  |
| - Duct Smoke Detectors |  |  |
| NFPA 90A: 9.3 | [Indicate type of duct smoke detectors required & provided, for example: Duct smoke detectors installed downstream of the air filters and ahead of any branch connections in air supply systems having a capacity greater than 2,000 cfm.] |  |
| - Elevators |  |  |
| UFC 3-600-01 [par. 4-13] IBC Chapter 30 ASME A17.1 NFPA 13 UFC 3-490-06 [par. 3-3.1] | [Indicate elevator type, construction, detection systems, and sprinkler requirements & provisions, for example: A holeless hydraulic type elevator is provided with 1 hr. rated shaft walls, sprinklers, smoke detectors, flow switches and necessary appurtenances for elevator machine room, top and pit of hoistway, see figure 4-4, UFC 3-600-01. See contract drawings for figure for type of elevator used. The elevator is not considered an egress component. Hoistway vent and elevator lobby not required for shaft penetrating up to 3 stories. Include hoistway pit entrapment protection per UFC 3-490-06: 3-3.1 requiring a door to an exit area.] |  |
| - Roof Access: |  |  |
| UFC 3-600-01 [par. 10-4] IBC Chapter 1011.12 | [Indicate requirements & provisions for roof access. If not required by code, user may request roof access from interior for convenience and in compliance with UFC 4-010-01 DoD Minimum Antiterrorism Standards for Bldgs.] |  |
| - Hazardous Locations |  |  |
| NFPA 70: NEC Articles 500 & 511 | [Indicate class and division of hazardous locations within the hangar bay, work bays, pits, and adjacent rooms. Indicate methods used to unclassified areas adjacent to classified locations such as corridors, offices, stockrooms, mechanical rooms, and electrical rooms. Indicate use of positive pressure or cut-off wall (to include door seals) to declassify areas adjacent to hazardous work areas.] |  |
| - Fire Dept. Vehicle Access |  |  |
| UFC 3-600-01 [par. 9-1] NFPA 1: 18.2.3.4.1 | [Indicate requirements and provisions for vehicle access to the building, for example: All weather ground access provided with widened/thickened sidewalks at 30 ft. from the building on two sides of the of all facilities more than two story building.] |  |
| - Fire Hydrant Installation |  |  |
| UFC 3-600-01 [par. 9-3.5] | [Indicate hydrant installation requirements and provisions including spacing based on building type.] |  |
| - Kitchen Cooking Exhaust Equipment |  |  |
| NFPA 101: 9.2.3, Chapters 12-42 NFPA 96 | [Indicate provision for kitchen cooking equipment in the project. Indicate extinguishing system required and provided. On contract drawings, show all interlocks with manual release switches, fuel shutoff valves, electrical shunt trips, exhaust fans, and building alarms.] |  |
| 5. EXISTING FACILITIES: |  |  |  |
| [If project scope does not include work to an existing facility, Section 5 can be indicated as not applicable.] |  |  |
| - Existing Facility Deficiency Upgrade: |  |  |
| UFC 1-200-01 [par. 3-3.1] NFPA 101: Chapters 12-42 | [Facilities as they exist prior to project, must meet NFPA 101 for existing occupancy. Entire facility must comply with the applicable existing occupancy chapter of NFPA 101 before beginning the project for work in existing facilities. A full facilities assessment is required to identify building deficiencies. Indicate what life safety deficiencies must be upgraded as part of the project or Establish management protocols to provide a level of life safety equivalent to that required by NFPA 101 for existing occupancies, until an upgrade project can be done. Management protocols must be in writing and approved by the BO/AHJ.] |  |
| - Work in Existing Facilities: |  |  |
| UFC 3-600-01 [par. 34-1.2.1] | [Conform to the requirements of the Building Rehabilitation chapter of NFPA 101 for design and construction of the project except as specified in UFC 3-600-01.] |  |
| NFPA 101, Chapter 43, Repair | [Identify the project area that apply to Repair, indicating how area meets NFPA 101 requirements.] |  |
| NFPA 101, Chapter 43, Renovation | [Identify the project area that apply to Renovation, indicating how area meets NFPA 101 requirements.] |  |
| NFPA 101, Chapter 43, Modification | [Identify the project area that apply to Modification, indicating how area meets NFPA 101 requirements.] |  |
| NFPA 101, Chapter 43, Reconstruction | [Identify project areas that apply to Reconstruction, indicating how area meets UFC and NFPA 101 requirements.] |  |
| UFC 3-600-01 [par. 34-1.2.8] | [Determine the total floor area will be reconfigured. If the total reconfigured floor plan exceed 50% of the total floor area, the entire floor must be brought up to the requirements for new construction in UFC 3-600-01 and NFPA 101.] |  |
| UFC 3-600-01 [par. 34-1.2.9] | [Determine if the total project cost exceed of the building total replacement value. If the total project cost exceed 50% of the total replacement value, the entire building must be brought up to the requirements for new construction in this UFC 3-600-01 and NFPA 101.] |  |
| NFPA 101, Chapter 43, Addition | Identify project areas that apply to Addition, indicating how area meets UFC and NFPA 101 requirements.] |  |
| - Change in Use Category: |  |  |
| UFC 3-600-01 [par. 34-1.3] | [Identify project areas that apply to Change in Use including change in occupancy, indicating how area meets UFC and NFPA 101 requirements.] |  |
| - Vacant Bldg. Category: |  |  |
| UFC 3-600-01 [par. 34-1.4] | [Identify project areas that apply to Vacant Bldg. category, indicating how area meets UFC and NFPA 101 requirements.] |  |
| - Phased Projects: |  |  |
| UFC 3-600-01 [par. 34-2] | [Indicate if this project includes multiple phases (potentially executed as separate projects) to the same existing facility within 5 years involving floor plan reconfiguration that will encompass more than 50% of the floor area or project cost exceeding 50% replacement value, triggering requirement for compliance with Reconstruction.] |  |
| - Cooking Areas: |  |  |
| UFC 3-600-01 [par. 34-3] | [Indicate if cooking areas are included and provision for compliance with UFC.] |  |
| - Electronic Equipment Areas: |  |  |
| UFC 3-600-01 [par. 34-5] | [Indicate if non-plenum rated cables exist under raised floors having no FE system and provision for compliance with UFC.] |  |
| - Automatic Sprinkler Systems: |  |  |
| UFC 3-600-01 [par. 34-1.2.6 & 9-7.2] | [Indicate compliance requirement and project's provision to meet the UFC.] |  |
| - Fire Alarm System: |  |  |
| UFC 3-600-01 [par. 34-1.2.8 & 9-18] | [Indicate compliance requirement and project's provision to meet the UFC. The notification appliances for the fire alarm and mass notification required to upgrade throughout the facility if reconfiguration exceed 50% of the floor plan.] |  |
| 6. MASS NOTIFICATION: |  |  |  |
| UFC 4-021-01 ECB 2018-17 | [Indicate mass notification system requirements and provisions including type of base-wide mass notification / communication system.] |  |
| 7. ACCESSIBILITY REQUIREMENTS: |  |  |  |
| ABA Chapters 1-10 | [Indicate accessibility requirements for the project, for example: "Facility shall be completely accessible in accordance with ABA. Fire alarm annunciators shall be in accordance with ABA." or "Facility is considered as being for able-bodied persons only, therefore, is not required to be fully accessible".] |  |
| 8. CERTIFICATION OF FIRE PROTECTION & LIFE SAFETY CODE REQUIREMENTS |  |  |
| Preparers of this document certify the accuracy and completeness of the Fire Protection and Life Safety features for this project indicated with the attached, completed signature forms. |  |  |

| ARCHITECT-ENGINEER (A-E) DESIGNS |  |  |
| --- | --- | --- |
| Certification of Fire Protection / Life Safety / Accessibility Code Requirements |  |  |
| [Insert Project Name and Location] [Insert Review Milestone (Preliminary, Interim, Final, or Corrected Final Review)] |  |  |
| Preparers of this document certify the accuracy, completeness, and incorporation of all required fire protection, life safety, and accessibility features in this project for the indicated milestone review. Signatures below indicate the project drawings, specifications and design analysis have been reviewed by QFPE and appropriate SMEs and is in compliance with the UFC 3-600-01 and referenced codes and standards. |  |  |
| Architect of Record [Insert typed name and provide signature above] |  | Date |
| Mechanical Engineer of Record [Insert typed name and provide signature above] |  | Date |
| Electrical Engineer of Record [Insert typed name and provide signature above] |  | Date |
| Civil Engineer of Record [Insert typed name and provide signature above] |  | Date |
| Qualified Fire Protection Engineer (QFPE) of Record [Insert typed name and provide signature above, affix QFPE stamp with date and signature below] |  | Date |

| IN-HOUSE DESIGNS |  |  |
| --- | --- | --- |
| Certification of Fire Protection / Life Safety / Accessibility Code Requirements |  |  |
| [Insert Project Name and Location] [Insert Review Milestone (Preliminary, Interim, Final, or Corrected Final Review)] |  |  |
| Preparers of this document certify the accuracy, completeness, and incorporation of all required fire protection, life safety, and accessibility features in this project for the indicated milestone review. Signatures below indicate the project drawings, specifications and design analysis have been reviewed by QFPE and appropriate SMEs and is in compliance with the UFC 3-600-01 and referenced codes and standards. |  |  |
| Technical Lead / Project Engineer Architect [Insert typed name and provide signature above] |  |  |
| Architect of Record [Insert typed name and provide signature above] |  | Date |
| Mechanical Engineer of Record [Insert typed name and provide signature above] |  | Date |
| Electrical Engineer of Record [Insert typed name and provide signature above] |  | Date |
| Civil Engineer of Record [Insert typed name and provide signature above] |  | Date |
| Qualified Fire Protection Engineer (QFPE) of Record [Insert typed name and provide signature above] |  | Date |