## Instructions
Energy Payback Calculations
Purpose: |  | The calculations derived within this workbook were originally developed for use by a retro-commissioning team to establish payback for various building repairs and modifications which would reap energy savings. Knowing the payback assists leaders in prioritizing when and where to make repairs.
The calculations can also be used by design engineers, energy managers, project managers, and field teams to help identify and prioritize energy-based improvements after field observations of building systems.
Notes: | 1) | The calculations presented in the following tabs are examples of the applications stated in the title, and any user should modify the data and calculations to meet the needs of their application.
| 2) | The user of this spreadsheet will need to be well versed in the field of HVAC and have an understanding of HVAC-related calculations. Accuracy of the output data depends on adaptation of data and formulas to match the situation in the facility being investigated. Assumptions in the calculations should be examined carefully for relevance.
| 3) | The individual worksheets are designed be stand alone documents, and can be copied and pasted into a Word document to be incorporated into a report for project teams and leadership to help in generating potential projects.
| 4) | Calculations, cost estimates, and actual design will require more detailed analyis and effort by qualified design professionals if they are implemented.
Instructions: | 1) | Do not delete the Input tab, as data from that tab is referenced in other tabs. Delete any other calculation tabs as desired.
| 2) | Insert specific data for your location in the Input tab; this will link the data to the calculation tabs.
| 3) | Use the Calc Index tab to find a particular topic and title of interest. Note that the numbering of the line items match the calculation tab numbering.
| 4) | Inputs into the calculation spreadsheets should only be necessary in the yellow cells unless formulas or format are being changed. Calculation outputs will appear in the green cells. The input/output colors are used to provide basic initial guidance and could require modification depending on the application. Be careful not to overwrite cells with formulas.
| 5) | Orange cells are links to the Input tab.
| 6) | Data shown from outside sources is typically denoted with a link to the source.
Cell Color Key
|  | Color | Description
|  | Yellow | Input
|  | Orange | Input (linked from Input tab)
|  | Green | Output (typically savings in kWh, BTU, $, or payback years)
|  | Blue | Used for spreadsheet formating
Grey
Source: | NAVFAC Washington Retro-Commissioning Team
Edited by NAVFAC Washington Facility Services Engineering Team
Calculations developed by CH2M-Hill were in part modifications of NAVFAC-generated spreadsheets and were delivered to NAVFAC Washington while under contract. CH2M-Hill spreadsheets have data modified by NAVFAC. Used by permission of CH2M-Hill.

## Calc Index
Calculation Sheet Index
# | Topic | Title | Application | Notes
1 | Thermostat | Thermostat Set Point Adjustment to Navy Standards Payback | HVAC
2 | Thermostat | Thermostat Set Point Adjustment to Navy Standards Payback (With Partition Load) | HVAC | Calculation developed by CH2MHill
3 | Thermostat | Thermostat Night and Weekend Setback Payback | HVAC
4 | Thermostat | Thermostat Night and Weekend Setback Payback (With Partition Load) | HVAC | Calculation developed by CH2MHill
5 | Demand Control Ventilation | Demand Control Ventilation (DCV) Control System Payback | HVAC | Calculation developed by CH2MHill
6 | Outside Air | Outside Air Reduction Payback | HVAC | Calculation developed by CH2MHill
7 | VAV Boxes | Restore VAV Boxes to Functional Operation Payback | HVAC | Calculation developed by CH2MHill
8 | Motors | Replace Motors with Electrically Commutated Motors Payback | HVAC | Calculation developed by CH2MHill
9 | Filters | Dirty Filter Replacement Payback | HVAC | Calculation developed by CH2MHill
10 | Coil Cleaning | Coil Cleaning Payback | HVAC | Calculation developed by CH2MHill
11 | Belts | Utilize Notched Belts on Air Handling Units Payback | HVAC | Calculation developed by CH2MHill
12 | Duct Leakage | Reduce Duct Air Loss Payback | HVAC
13 | Pipe Insulation | Insulate Domestic Hot Water Piping Payback | HVAC
14 | Electric Baseboard | Clean Electric Baseboard/Seasonal Lockout/Unoccupied Cutoff Payback | HVAC
15 | Lighting/Fans | Bathroom Motion Sensor Addition for Fan and Lights Payback | HVAC | Calculation developed by CH2MHill
16 | Valves | Repair Non-Closing HHW Valve on Coil Payback | HVAC | Calculation developed by CH2MHill
17 | Valves | Repair Non-Closing CHW Valve on Coil Payback | HVAC
18 | Window Units | Replace Window Type Units With Mini Split Ductless Units Payback | HVAC
19 | Compressed Air | Repair Compressed Air Leaks Payback | HVAC | Calculation developed by CH2MHill
20 | Fans | Add Destratification Fans Payback | HVAC | Calculation developed by CH2MHill
21 | Fans | Add Low Speed Ceiling Fan Payback | HVAC
22 | Windows | Add HVAC Smart Relay Switch (HSRS) to Windows Payback | Enclosure
23 | Windows | Add Heat Shrink Plastic Film to Windows Payback | Enclosure
24 | Windows | Clean Glass Block/Daylighting Windows Payback | Enclosure
25 | Windows | Add Reflective Film Windows Payback | Enclosure
26 | Windows | Window Replacement Payback | Enclosure | Calculation developed by CH2MHill
27 | Doors | Repair Weatherstripping at Outside Doors Payback | Enclosure
28 | Doors | Coordinate Open Time for Automatic Door Openers at Vestibule Payback | Enclosure
29 | Doors | Add Air Curtain to Entrance Doors Payback | Enclosure
30 | Doors | Replace Vestibule Doors with Revolving Door Payback | Enclosure
31 | Plant Trees | Plant Trees to Reduce Glare and Provide Shade Payback | Enclosure
32 | Lighting | Add Daylighting Sensors Payback | Lighting | Calculation developed by CH2MHill
33 | Lighting | Install Occupancy Sensors Payback | Lighting
34 | Lighting | Reduce Lamp Wattage Payback | Lighting | Calculation developed by CH2MHill
35 | Lighting | Replace Outdoor Lights With LED Payback | Lighting
36 | Lighting | Replace Indoor Lights With LED Payback | Lighting
37 | Plumbing | Upgrade Plumbing Fixtures Payback | Plumbing | Calculation developed by CH2MHill
38 | Water Heater | Replace Electric Hot Water Heater With Gas Payback | Kitchen
39 | Kitchen | Convert Electric Kitchen Equipment to Gas Payback | Kitchen
40 | Kitchen | Replace Kitchen Pre-Rinse Spray Valve with Water Saving Model Payback | Kitchen
41 | Kitchen | Replace Kitchen Hood Exhaust System With Gas-fired Makeup Air Unit Payback | Kitchen
42 | Condensing Unit | Move Indoor Condenser Outside Payback | Kitchen

## Input
General Information
Building Number: | 1000
Building Name | Sample Building
Base Name | Navy Base
Location | Washington DC
Building Type | School
Date | 2023-01-01
Utility Cost Data
Electricity | 0.09 | $/kWh | 26.3775 | $/Mbtu
Natural Gas | 0.8 | $/therm | 8 | $/Mbtu
Coal | x | $/ton
Fuel Oil | x | $/gal | 22.42 | $/Mbtu
Propane | x | $/gal | 14.35 | $/Mbtu
Steam |  |  | 33 | $/Mbtu
High Temp HW |  |  | 33 | $/Mbtu
Chilled Water |  |  | 33 | $/Mbtu
Water | 4 | $/kgal
Sewer | 4 | $/kgal
Conversion Factors:
1 deg F ∆T x 1 lb of water = |  | 1 | BTU
1 Gallon water = |  | 8.33 | lbs
1 BTU = |  | 1e-05 | Therms
1 therm = |  | 100000 | BTUs
Conversion of KWh to BTU |  | 3412
conversion of BTU to KWh: |  | 0.00029307
Specific heat of water: |  | 1
Efficiency Electric Heat |  | 100%
Efficiency Gas |  | 95%
Convert Watts to Amps (watts/ volts)
Convert Amps to Watts (amps x volts)

## 1-TStatSP
Thermostat Set Point Adjustment to Navy Standards Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  | 2023-01-01
Navy Standard Thermostat Settings: 68 degrees F winter heating; 78 degrees F summer cooling. Current settings estimated from Data Logger Readings and settings found at building to be 72 deg average. Calculation assumes entire building with one thermostat zone - for separate partition zones use tab number 2.
Area of building | 11534 | Number of floors | 2 | Height (feet) | 14 | Average Length | 101 | Average Width | 64
Q = A x U x (Ti - To) |  |  |  |  | Estimated Average U value: |  |  | 0.15
Q = Total hourly rate of heat loss |  |  |  |  | Surface Area: |  |  | 10387 | sq. ft.
U = overall heat transfer coef. Btu/hr sq ft |  |  |  |  | Total heat loss/ year = Area x U value x (HDD or CDD) x 24 hrs/day
A = Net area
Ti = Inside design temp |  |  |  |  | Total yearly Heat Loss @ 72 deg. F: |  |  | 233969252.4 | BTUs
To = Outside design temp |  |  |  |  | Total yearly Heat Loss @ 68 deg. F: |  |  | 195342076.8 | BTUs
[7 empty] | Savings: | 38627175.6 | BTUs
Heating Degrees Days @ 72 deg. F: |  |  | 6257
Heating Degrees Days @ 68 deg. F: |  |  | 5224 |  | Total yearly cooling Loss @ 72 deg. F: |  |  | 27371822.4 | BTUs
Cooling Degrees Days @ 72 deg. F: |  |  | 732 |  | Total yearly cooling Loss @ 78 deg. F: |  |  | 11741464.8 | BTUs
Cooling Degrees Days @ 78 deg. F: |  |  | 314 |  |  |  | Savings: | 15630357.6 | BTUs
(source: www.degreedays.net (using temperature data from www.wunderground.com)
[6 empty] | Total Savings |  | 54257533.2 | BTUs
Convert BTUs to KWh: 1 BTU/hr = 0.00029307107 kW
Cost Information: |  |  |  |  | KWh Used at existing settings: |  |  | 76591.5084 | KWh
Labor for Control's Tech to adjust and re-program as required, verify as needed: |  |  |  |  | KWh Used at Navy Standard Settings: |  |  | 60690.1951 | KWh
[7 empty] | Savings: | 15901.3133 | KWh
|  | 4000 |  |  | Cost per KWh in $ |  | 0.09 | 1431.1182 | Savings
Payback = cost savings / cost of implementation
[7 empty] | Payback= | 2.795 | years

## 2-TStatSPPart
Thermostat Set Point Adjustment to Navy Standards Payback (With Partition Load)
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Navy Standard Thermostat Settings: 68 degrees F winter heating; 78 degrees F summer cooling. Current settings estimated from Data Logger Readings and settings found at building. If only exterior walls, partition load is not applicable.
Floor (Roof) Area (SF) | 81000 | Number of floors | 1 | Wall Height (ft) | 48 | Average Length (ft) | 405 | Average Width (ft) | 105
Q = A x U x ∆T + Partition Load |  |  |  | ASHRAE |  |  |  | Estimated Average U value: | 0.1 | (R-10)
Q = Total hourly rate of heat loss |  |  |  | mo | tavg
U = overall heat transfer coef. Btu/hr sq ft |  |  |  | 1 | 36.9 |  |  | Portion of building heated: | 100%
A = Net area |  |  |  | 2 | 38.9 |  |  | Average Heating Efficiency (COP): | 1 | (dist. steam)
Ti = Inside design temp |  |  |  | 3 | 47.1 |  |  | Surface Area (heating): | 129960 | sq. ft.
To = Outside design temp |  |  |  | 4 | 56.9
|  |  |  | 5 | 65.9 |  |  | Portion of building cooled: | 100%
| Heating Degrees Days @ 70 deg. F: | 5336 |  | 6 | 75.2 |  |  | Average Cooling Efficiency (COP): | 1 | (dist. CHW)
| Heating Degrees Days @ 68 deg. F: | 4865 |  | 7 | 79.8 |  |  | Surface Area (cooling): | 129960 | sq. ft.
| Cooling Degrees Days @ 75 deg. F: | 492 |  | 8 | 78.2
| Cooling Degrees Days @ 78 deg. F: | 290 |  | 9 | 71.1 |  |  | Total yearly Heat Loss @ 70 deg. F: | 1664319744 | BTUs
(source: www.degreedays.net (using temperature data from www.wunderground.com) |  |  |  | 10 | 59.3 |  |  | Total yearly Heat Loss @ 68 deg. F: | 1517412960 | BTUs
|  |  |  | 11 | 49.5 |  |  | Heating Savings: | 146906784 | BTUs
|  |  |  | 12 | 39.8 |  |  |  | 146.9068 | MBtu
Estimated Partition Load
|  | Partition Area | 0 | sq ft |  |  |  | Total yearly Cooling Loss @ 75 deg. F: | 153456768 | BTUs
|  | Partition Average U-Value | 0.1 | Btu/sq ft-°F | (R-10) |  |  | Total yearly Cooling Loss @ 78 deg. F: | 90452160 | BTUs
|  | Season: | Cooling | Heating |  |  |  | Cooling Savings: | 63004608 | BTUs
|  | Equivalent Full Load Hours: | 1320 | 2061 | hrs |  |  |  | 63.0046 | MBtu
|  | Average Ambient Temperature: | 74 | 47 | °F
|  | Estimated Average Adjacent Space Temperature: | 79 | 70 | °F |  | Heating Cost per MBtu: | 33 | 4847.9239 | Savings
|  | Current Setpoints: | 72 | 68 | °F |  | Cooling Cost per kWh: | 33 | 2079.1521 | Savings
|  | Adjusted Setpoints: | 78 | 68 | °F |  |  | Total Cost Savings: | 6927.0759 | Savings
|  | Estimated Partition Heat Gain/Loss (current setpoints): | 0 | 0 | Btu
|  | Estimated Partition Heat Gain/Loss (adjusted setpoints): | 0 | 0 | Btu | Total heat or cooling loss /year =
[Area x U value x (HDD or CDD) x 24 hrs/day] / efficiency
[6 empty] | Convert BTUs to kWh: |  | 1 BTU = | 0.00029307 | kWh
Cost Information: |  |  | # of t-stats = | 11
Labor for Controls Tech to adjust thermostat and heating SAT setpoints as required, verify as needed: 1 hr/tstat or point @ $100/hr | [6 empty] | Payback = cost savings / cost of implementation
[5 empty] | 1100 |  |  | Simple Payback = | 0.1588 | years

## 3-NightWkdSetback
Thermostat Night and Weekend Setback Payback
Building # | 1000 | Sample Building |  |  |  | Navy Base |  |  | Washington DC |  |  | 2023-01-01
Navy Standard Thermostat Settings: 68 degrees F winter heating; 78 degrees F summer cooling. Proposed setbacks are for building based on average closing time of 10:00 pm until 9:00 am. User should modify to reflect actual building operations.
Area of building | 11534 | Number of floors | 2 | Height per fl. (feet) | 14 | Average Length | 101 | Average Width | 64
| Q = A x U x ∆T | [5 empty] | Estimated Average U value: |  |  | 0.12
| Q = Total hourly rate of heat loss | [5 empty] | Surface Area: |  |  | 10387 | sq. ft.
| U = overall heat transfer coef. Btu/hr sq ft | [5 empty] | Total heat loss/ year = Area x U value x ∆T x hours
| A = Net area |  | ∆T = temp difference |  |  |  | Assume setbacks not relevant in swing months
| To Convert BTUs to KWh: 1 BTU/hr = |  |  |  | 0.00029307 | KWh | Cost per KWh in $ |  | 0.09
Heating Months | Cooling Months | Swing Months | Baseline Days/ month | subtract weekends days/mo | Baseline Hours/ day | Active Hours/ day | Current Heating | Current Cooling | Navy Standard Heating | Navy Standard Cooling | Prop. Setback Heating | Prop. Setback Cooling
4 | 4 | 4 | 30 | 22 | 24 | 16 | 72 | 72 | 68 | 78 | 60 | 80
Existing Building Settings | Mode | Hours building at normal temperature |  |  |  | ∆T |  |  | MBTU Savings Calculations
|  | No setback | Night Setback | Weekend Setback | Night + Wkd | Current Temp. | Prop. Set | ∆T | w/night Setback | w/Wkd Setback | Night + wkd
| Heating | 2880 | 1920 | 2112 | 1408 | 72 | 60 | 12 | 14358.9888 | 11487.191 | 22017.1162
| Cooling | 2880 | 1920 | 2112 | 1408 | 72 | 80 | 8 | 9572.6592 | 7658.1274 | 14678.0774
| Combined Heating and Cooling MBTU savings per year | [7 empty] | 23931.648 | 19145.3184 | 36695.1936
| KWh Savings per Year | [7 empty] | 7013.6737 | 5610.9389 | 10754.2997
| Cost Savings per Year | [7 empty] | 657.8826 | 526.3061 | 1008.7533
| Payback (years) | [7 empty] | 4.5601 | 5.7001 | 2.974
Navy Standard Settings | Mode | Hours building at normal temperature |  |  |  | ∆T |  |  | MBTU Savings Calculations
|  | No setback | Night Setback | Weekend Setback | Night + Wkd | Current Temp. | Prop. Set | ∆T | w/night Setback | w/Wkd Setback | Night + wkd
| Heating | 2880 | 1920 | 2112 | 1408 | 68 | 60 | 8 | 9572.6592 | 7658.1274 | 14678.0774
| Cooling | 2880 | 1920 | 2112 | 1408 | 78 | 80 | 2 | 2393.1648 | 1914.5318 | 3669.5194
| Combined Heating and Cooling MBTU savings per year | [7 empty] | 11965.824 | 9572.6592 | 18347.5968
| KWh Savings per Year | [7 empty] | 3506.8368 | 2805.4695 | 5377.1498
| Cost Savings per Year | [7 empty] | 328.9413 | 263.153 | 504.3767
| Payback (years) | [7 empty] | 9.1202 | 11.4002 | 5.9479
Cost Information: |  | Labor for Control's Tech to adjust and re-program as required, verify as needed: | [5 empty] | 3000

## 4-NightWkdSetbackPart
Thermostat Night and Weekend Setback Payback (With Partition Load)
Building # | 1000 | Sample Building |  |  | Navy Base |  |  | Washington DC |  |  | 2023-01-01
Heating system for zones served by AHU-1 and -02 are controlled by non-programmable thermostats - 9 total zones. Install pneumatic programmable thermostats with night/weekend setback temperatures.
| Floor (Roof) Area (SF) | 80843 | Number of floors | 1 | Wall Height (ft) | 48 | Average Length (ft) | 405 | Average Width (ft) | 105
| Q = A x U x ∆T + Partition Load | [7 empty] | Estimated Average U value: | 0.1 | (R-10)
Q = Total hourly rate of heat loss |  |  |  | A = Net area |  |  |  |  | Surface Area: | 91485 | sq. ft.
U = overall heat transfer coef. Btu/hr sq ft |  |  |  | ∆T = temp difference
[9 empty] | cooling COP | 1
|  | To Convert BTUs to KWh: 1 BTU = | 0.00029307 |  | KWh |  |  |  | heating COP | 1
|  | Cooling Cost per MBtu | 33 |  |  | Estimated Partition Load
|  | Heating Cost per MBtu | 33 | [5 empty] | Partition Area: | 0 | sq ft
[9 empty] | Partition Average U-Value: | 0.1 | Btu/sq ft-°F | (R-10)
| Total heat loss/ year = Area x U value x ∆T x hours | [8 empty] | Cooling | Heating
| Assume setbacks not relevant in swing months | [7 empty] | Average Ambient Temperature: | 74 | 47 | °F
[9 empty] | Estimated Average Adjacent Space Temperature: | 79 | 70 | °F
| Heating Months | Cooling Months | Swing Months | Baseline Days/ month | With wkd setback days/mo | Baseline Hours/ day | Active Hours/ day | Current Heating | Current Cooling | Prop. Setback Heating | Prop. Setback Cooling
| 5 | 5 | 2 | 30 | 30 | 24 | 12 | 70 | 75 | 60 | 80
| Mode | On Hours |  |  |  | ∆T |  |  | MBTU Savings Calculations
|  | No setback | Night Setback | Wkd Setback | Night + Wkd set on hours | Current Temp. | Prop. Set | ∆T | w/night Setback | w/Wkd Setback | Night + wkd
| Heating | 3600 | 1800 | 2571.4286 | 1285.7143 | 70 | 60 | 10 | 164.673 | 94.0989 | 211.7224
| Cooling | 3600 | 1800 | 2571.4286 | 1285.7143 | 75 | 80 | 5 | 82.3365 | 47.0494 | 105.8612
| Heating MBtu Savings per year | [7 empty] | 164.673 | 94.0989 | 211.7224
| Cooling MBtu Savings per Year | [7 empty] | 82.3365 | 47.0494 | 105.8612
| Cost Savings per Year | [7 empty] | 8151.3135 | 4657.8934 | 10480.2602
| Simple Payback (years) | [7 empty] | 0.49379 | 0.86412 | 0.38406
Cost Information:
| Cost to reprogram existing programmable thermostats, and to install programmable thermostats and program accordingly. | [5 empty] | # of Tstats to replace = |  |  | 9 | 3825
[7 empty] | # of Tstats to reprogram = |  |  | 2 | 200
| Installed Cost for Setback T-stat |  |  |  | 425 | [5 empty] | 4025
| Reprogram T-stat |  |  |  | 100
Note on D5: mbryan1: Building area minus kitchen/serving area.

## 5-DCV
Demand Control Ventilation (DCV) Control System Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
For each of the 2 AHUs, provide DCV to reduce outside air flow during time periods when not required. Please note that this measure assumes outside air is returned to normal operation as part of retro-commissioning implementation. Minimal outside air observed as part of test, adjust, and balance performed on building.
Total Estimated Building Ventilation |  |  |  |  | Estimated Ventilation Savings
Building Size | 80843 | sf |  |  | Minimum Outside Air Setpoint |  |  | 0.125 | cfm/sf
Building Height |  | feet per floor |  |  | Typical DCV Savings 20%-70% |  |  | 45% | Outside Air Volume savings from DCV
Building Volume | 0 | cubic feet of volume |  |  | Typical Building Energy Savings 2%-7% |  |  | 4.5% | Building Energy Savings (for cross check)
Air Changes Per Hour |  | air change/hr for typical bldg |  |  | Typical DCV Ventilation Savings |  |  | 0.053326 | cfm/sf
Air Volume Changed Per Hour | 0 | cubic feet/hr |  |  | DCV Savings |  |  | 4311 | cfm
Air Volume Changed Per Minute | 9580 | cfm |  |  | Cooling |  |  | 1 | COP estimated efficiency
Air Ventilation per Square Foot | 0.1185 | cfm/sf |  |  | Heating |  |  | 1 | COP estimated efficiency
[5 empty] | V (CFM) = |  |  | 4311 | cfm
heat capacity of air (Btu/ CFt.)= |  | 0.018 |  |  | Annual Heating degrees days: |  |  | 4865
Q = .018 x V x temp dif. |  |  |  |  | Annual Cooling degree days: |  |  | 290
Qyr = .018 x cubic ft. /day x degree days
coversion of Btu to kWh: | 1 Btu = | 0.00029307 | kWh |  | MBtu Heating Savings |  |  | 543.6205 | MBtu
[5 empty] | Cost Savings |  |  | 17939.4781
cost per cooling MBtu: |  | 33 | CHW |  | MBtu Cooling Savings |  |  | 32.4049 | MBtu
cost per heating MBtu: |  | 33 | Steam |  | Cost Savings |  |  | 1069.3625
MBTU heating loss per year |  | 543.6205 | MBtu |  | Total Cost Savings |  |  | 19008.8406
MBTU cooling loss per year |  | 32.4049 | MBtu
*http://ibpsa-boston.com/minutes/IBPSAboston-presentations_2011-09-16_Gowri.pdf |  |  |  |  | Project cost: |  |  | 17429.1
http://www.cedengineering.com/upload/Heat%20Loss%20Calculations%20and%20Principles.pdf |  |  |  |  | Simple Payback: |  |  | 0.91689 | Years
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | # of RTUs | Total
| DDC-Pneumatic interface |  |  | EA | 1 | 1600 | 2200 | 0 | 3800 | 2 | 7600
23 09 23.10 1040 | AO: Electric DAMPER ACTUATION |  |  | Point | 2 | 250 | 350 | 0 | 600 | 2 | 2400
23 09 23.10 0160 | AI: Duct Static Pressure Duct Mount CO2 Sensor |  |  | Point | 1 | 400 | 500 | 0 | 900 | 2 | 1800
23 09 23.10 4500 | Engineering Labor |  |  | Point | 3 | 60 | 98 | 0 |  | 2 | 0
23 09 23.10 4600 | Calibration Labor |  |  | Point | 3 | 80 | 100 | 0 | 180 | 2 | 1080
23 09 23.10 4700 | Start-up Check Out |  |  | Point | 3 | 80 | 100 | 0 | 180 | 2 | 1080
23 09 23.10 8160 | Demand limiting |  |  | Point | 3 | 15 | 20 | 0 | 35 | 2 | 210
[5 empty] | Subtotal |  |  |  | 5695 |  | 14170
[5 empty] | Contingency |  |  |  | 0.08 |  | 1133.6
[5 empty] | OH |  |  |  | 0.05 |  | 708.5
[5 empty] | Profit |  |  |  | 0.1 |  | 1417
[5 empty] | Total | [5 empty] | 17429.1
Note on G7: Example: CEC Technical Options Guidebook for Enhanced Automation, May 2002
Note on G8: Example: CEC Technical Options Guidebook for Enhanced Automation, May 2002
Note on C11: mbryan1: From Design Drawings

## 6-OA
Outside Air Reduction Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Outside Air Reduction if done correctly to provide healthy code complient outside air in quanties that allow slight building pressurization without adding too much is a great energy savings strategy for minimal cost. AHU-1 current outside airflow rate is 815 cfm. Current space served by AHU-1 is office space on the first floor, requiring considerably less outside air. Reduce outside airflow for AHU-1 to 200 cfm.
OA Reduction Calculation:
| Qyr = heat capacity of air x cubic ft. /day x degree days | [6 empty] | Excess OA (CFM) = | 615 | cfm
|  | heat capacity of air (Btu/ CFt.) = | 0.018 |  |  |  |  | Annual Heating degrees days: | 4865
[8 empty] | Annual Cooling degree days: | 577
|  | Measured Total OA = | 815 | cfm
|  | Design Total OA = | 200 | cfm |  |  |  | Heating Energy Savings: | 77551992 | BTUs
[9 empty] | 77.552 | MBtu
|  | conversion of Btu to KWh: | 0.00029307 |  |  |  |  | Heating Cost Savings: | 2559.2157
|  | Heating cost per MBtu: | 33 |  |  |  |  | Cooling Energy Savings: | 9197841.6 | BTUs
|  | Cooling cost per kWh: | 33 | [5 empty] | 898.5404 | kWh
|  | Heating COP: | 1 |  |  |  |  | Cooling Cost Savings: | 29651.8341
|  | Cooling COP: | 3
[8 empty] | Total Energy Cost Savings: | 32211.0498
*http://ibpsa-boston.com/minutes/IBPSAboston-presentations_2011-09-16_Gowri.pdf | [7 empty] | Implementation Cost: | 971.7
*http://www.cedengineering.com/upload/Heat%20Loss%20Calculations%20and%20Principles.pdf | [7 empty] | Simple Payback: | 0.030167 | Years
RS Means | Description |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
25 05 93 10 | Air balancing rooftop Unit |  |  | EA | 1 | 325 | 450 | 15 | 790 | 790
|  |  |  | EA | 0 | 0 | 180 | 0 | 180 | 0
|  |  |  | EA | 0 | 0 | 180 | 0 | 180 | 0
[5 empty] | Subtotal |  |  |  | 1150 | 790
[5 empty] | Contingency |  |  |  | 0.08 | 63.2
[5 empty] | OH |  |  |  | 0.05 | 39.5
[5 empty] | Profit |  |  |  | 0.1 | 79
[5 empty] | Total |  |  |  |  | 971.7

## 7-VAV
Restore VAV Boxes to Functional Operation Payback
Building # | 1000 | Sample Building | Navy Base |  |  | Washington DC |  |  |  | 2023-01-01
Restoring VAV boxes to proper operation not only saves energy but is important for occupant comfort. VAV boxes have been over-ridden open, closed, or reversed operation versus what the controls system appears to be requesting.
[5 empty] | Existing: | Loading Estimate | % | 57.24% |  | $/kWh | 0.09109
Energy Use: |  | E = M*C*H*L/EF |  |  | Proposed: | Average Loading | % | 41%
M = motor horsepower |  |  | 25 | hp
C = conversion constant, 0.746 kW/hp |  |  | 0.746 | kW/hp
H = annual hours of operation |  |  | 8760 | hours |  |  |  |  | Existing Estimated Energy Consumption | 100559.9297 | kWh/yr
L = estimated loading, % |  |  | 100% | [5 empty] | Proposed Estimated Energy Consumption | 72018.6695 | kWh/yr
EF = motor efficiency, % |  |  | 93% | [5 empty] | Estimated Energy Savings | 28541.2602 | kWh/yr
|  | VAV AHU count | 1 | [5 empty] | Total KWh per year saved: | 28541.2602 | kWh
|  | VAV Box counts | 23 | [5 empty] | Cost of KWh Saved: | 2599.8234
|  | VAV Boxes Affected | 25% | [5 empty] | Simple payback: | 5.7435 | years
Cost Estimate:
|  | VAV balancing. Assumes control work is required on approximately 1/4 of VAV boxes to return to normal operation. Assumes work occurs after functionality returned to overall building controls. | [7 empty] | 14932.2
Division | Description |  |  |  | unit | QTY | material | labor | Equip. | Per unit | Total
230923.1 | VAV Terminal Box Controls |  |  |  | ea | 6 | 575 | 775 | 0 | 1350 | 8100
230593.1 | Balancing, Built-up Variable Volume 2400 subdiv. |  |  |  | ea | 1 | 1100 | 1500 | 0 | 2600 | 2600
230593.1 | Balancing, Built-up Variable Volume 3000 subdiv. |  |  |  | ea | 12 | 50 | 70 | 0 | 120 | 1440
[6 empty] | Subtotal |  |  |  | 4070 | 12140
[6 empty] | Contingency |  |  |  | 8% | 971.2
[6 empty] | OH |  |  |  | 5% | 607
[6 empty] | Profit |  |  |  | 10% | 1214
[6 empty] | Total |  |  |  |  | 14932.2
Note on J5: Ruffel, Eric/DEN: assumes 80% of flow consistent with VFD reading at time of visit. 2.5 exponent used vs 3.0.
Note on J6: Ruffel, Eric/DEN: assumes 70% of flow can be achieved. TAB confirms some VAVs wired full open or programming reversed. 2.5 exponent used vs 3.0.

## 8-ECMotors
Replace Motors with Electrically Commutated Motors Payback
Building # | 1000 | Sample Building |  |  |  | Navy Base |  |  | Washington DC |  |  | 2023-01-01
30 total rooms with FCUs with 1/3 hp motors. 3 total rooms with FCUs with 3/4 hp motors. | [11 empty] | Cost Per KWh | 0.09
Energy Use: |  |  |  | M = | motor horsepower |  |  |  | Note: Cost for EC motors was based on Evergreen IM motors. Evergreen produces two size motors. 1/2 HP motor can replace motors from 1/5 to 1/2 HP PSC motors, 1 HP motor that can replace motors 1/2 to 1 HP PSC motors, etc.
|  |  |  | C = | conversion constant, |  | 0.746 | kW/hp
E = M*C*H*L/EF |  |  |  | H = | annual hours of operation
|  |  |  | L = | estimated loading, %
|  |  |  | EF = | motor efficiency, %
Motor HP | Qty | Annual Run Hours | Estimated Loading | Motor Efficiency |  | Estimated energy consumption per motor |  | Energy req'd to offset motor heat per motor (kWh) | Estimated energy savings per motor (kWh) | Total energy savings (kWh) | Total cost savings | Imp. cost | Simple Payback (yrs)
|  |  |  | PSC | ECM | Existing (PSC) (kWh) | Proposed (ECM) (kWh)
0.2 | 0 |  |  | 51% | 80% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.25 | 0 |  |  | 55% | 80% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.33333 | 30 | 3615 | 80% | 60% | 80% | 1198.5733 | 898.93 | 143.8288 | 443.4721 | 13304.164 | 1197.3748 | 24300 | 20.2944
0.5 | 0 |  |  | 68% | 80% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.75 | 3 | 3615 | 80% | 72% | 80% | 2247.325 | 2022.5925 | 129.4459 | 354.1784 | 1062.5353 | 95.6282 | 2655 | 27.7638
1 | 0 |  |  | 68% | 80% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Total Energy Savings: | 14366.6993 | kWh |  |  | Total Implementation Cost: | 29889
[6 empty] | Total Energy Cost Savings: | 1293.0029 |  |  |  | Simple Payback: | 23.116 | yrs
Means | Description |  |  |  | HP | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
26 00 00 | ECM motor |  |  |  | 0.2 | ea | 0 | 375 | 425 | 10 | 810 | 0
26 00 00 | ECM motor |  |  |  | 0.25 | ea | 0 | 375 | 425 | 10 | 810 | 0
26 00 00 | ECM motor |  |  |  | 0.33333 | na | 30 | 375 | 425 | 10 | 810 | 24300
26 00 00 | ECM motor |  |  |  | 0.5 |  | 0 | 375 | 425 | 10 | 810 | 0
26 00 00 | ECM motor |  |  |  | 0.75 |  | 3 | 450 | 425 | 10 | 885 | 2655
26 00 00 | ECM motor |  |  |  | 1 |  | 0 | 450 | 425 | 10 | 885 | 0
[7 empty] | Subtotal |  |  |  | 2430 | 24300
| PSC (HP) | Efficiency* | ECM (HP) | Efficiency** |  |  | Contingency |  |  |  | 8% | 1944
| 0.2 | 51% | 0.2 | 80% |  |  | OH |  |  |  | 5% | 1215
| 0.25 | 55% | 0.25 | 80% |  |  | Profit |  |  |  | 10% | 2430
| 0.33333 | 60% | 0.33333 | 80% |  |  | Total |  |  |  |  | 29889
| 0.5 | 68% | 0.5 | 80%
| 0.75 | 72% | 0.75 | 80% |  | * http://www.baldor.com/catalog
| 1 | 68% | 1 | 80% |  | ** https://www.genteqmotors.com/Products/Aftermarket/Evergreen_IM/

## 9-Filters
Dirty Filter Replacement Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  | 2023-01-01
The air filters for RAC-1 and 2 located on the roof of A and B Wings were highly loaded. Assume present loading produces a pressure drop of 1.5 in. wg across the filters. Discipline best practice suggests maximum pressure drop due to loaded filters to be 0.75 in.w.g. Excessive pressure drop results in increase energy use. Total airflow and base static pressure are from TAB report.
Basic Equation | kWh savings = ((Cfm x delta PD x .746)/(6345 x efficiency)) x hours | [6 empty] | $/kWh | 0.09
kWh = Fan Annual Energy Consumption
Cfm = Air flow rate
delta PD = (measured - design pressure) drop across filters, in. w.g.
6345 = constant
efficiency = fan and motor efficiency
|  | Air Flow Rate | 19107 | cfm |  | Cross-check for reasonableness:
|  | Existing PD | 2.03 | in. w.g. |  |  | 50 | hp motor | cumulative
|  | Proposed PD | 1.28 | in. w.g. |  |  | 326748 | kWh/yr 100% loading
|  | Fan & motor efficiency | 0.5 | estimated |  | Assume: | 40% | loaded presently
|  | Run hours | 4380 | Hours |  | VFD | 35% | loaded potential
|  | Annual kWh savings | 14759.2767 | kWh |  |  | 130699.2 | kWh presently
[7 empty] | 114361.8 | kWh with clean filters
|  | Annual Cost Savings | 1328.3349 |  |  |  | 16337.4 | Savings
hightech.lbl.gov/documents/.../cr.../HVACAirSystems_LowPDrop.doc
| Cost: | Typically included in PM regime. Background for this loaded filter may require additional activity to prevent in future.
Note on E13: mbryan1: Average PD between RAC-1 (2.23 in wg)and RAC-2 (1.83 in wg)

## 10-CoilCleaning
Coil Cleaning Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  | 2023-01-01
The cooling and heating coils for the Dectron Pool AHU were dirty. Conservatively, assume dirty coils impact performance by increasing air pressure drop across each coil by 5% and decreasing heat transfer effectiveness by 10%. Assume mode during run hours is 1/2 cooling and 1/2 heating.
Basic Equation | kWh savings = ((Cfm x delta PD x .746)/(6345 x efficiency)) x hours | [6 empty] | $/kWh: | 0.09
| kWh = Fan Annual Energy Consumption | [6 empty] | $/MBtu: | 8
Cfm = Air flow rate
| delta PD = (measured - design pressure) drop across filters, in. w.g. | [6 empty] | Cooling COP: | 3
| 6345 = constant | [6 empty] | Heating COP: | 0.85
efficiency = fan and motor efficiency
Convert: | 1 Btu = | 0.00029307 | kWh
Efficiency Deficit (%)
| Air Flow Rate: | 15000 | cfm | TAB Report |  |  | Pressure drop: | 5%
| PD across Coils (Dirty): | 2 | in. w.g. | TAB Report |  |  | Heat Transfer: | 10%
| PD across Coils (Clean/Design): | 1.9 | in. w.g.
| Combined fan+motor efficiency: | 0.5 | estimated |  |  | Estimated Design Coil Capacity:
| Run hours: | 4732 | Hours | Only when occupied |  |  | Cooling: | 486 | mbh
| Annual kWh savings: | 3089.8156 | kWh |  |  |  | Heating: | 810 | mbh
For Estimating: | [5 empty] | Energy Use: | Clean/Design | Dirty
| Coil Face Area: | 30 | sf |  |  | Cooling: | 1149.876 | 1277.64 | MBtu
| # of coils: | 2 |  |  |  | Heating: | 1916.46 | 2129.4 | MBtu
| Total Coil Face Area: | 60
[7 empty] | Cooling Energy Savings: | 127.764 | MBtu
| Electrical Energy Savings: | 15571.1263 | kWh | (cooling and fan energy) |  |  |  | 12481.3107 | kWh
| Thermal Energy Savings: | 250.5176 | MBtu | (heating energy) |  |  | Heating Energy Savings: | 250.5176 | MBtu
| Total Energy Savings: | 303.6485 | MBtu
[7 empty] | Total Annual Cost Savings: | 3405.5425
| Total Electrical Cost Savings: | 1401.4014 |  |  |  |  | Implementation Cost: | 29527.38
| Total Thermal Cost Savings: | 2004.1412 |  |  |  |  | Simple Payback: | 8.6704 | years
Reference ASHRAE Journal article: http://www.ashrae.org/File%20Library/docLib/Journal%20Documents/2006November/28882montgomery.pdf
Description |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Commercial Coil Cleaning |  |  | SF | 60 | 150 | 250 | 0.1 | 400.1 | 24006
|  |  |  | Subtotal |  |  |  | 400.1 | 24006
|  |  |  | Contingency |  |  |  | 0.08 | 1920.48
|  |  |  | OH |  |  |  | 0.05 | 1200.3
|  |  |  | Profit |  |  |  | 0.1 | 2400.6
|  |  |  | Total |  |  |  |  | 29527.38
Note on C5: Ruffel, Eric/DEN: hightech.lbl.gov/documents/.../cr.../HVACAirSystems_LowPDrop.doc
Note on D21: mbryan1: Assume coil face velocity of 500 fpm

## 11-AHUBelts
Utilize Notched Belts on Air Handling Units Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  | 2023-01-01
Replace worn belts with notched belts (approximately 2% improvement) and tighten loose belts (approximately 5% improvement). Note: the cost estimating is based on the difference in cost between replacing with standard belt and cost for replacing with higher efficiency cogged belts. Calculation is configured as a procurement policy.
[6 empty] | Energy Rate | 0.09 | $/kWh
Belts to be Replaced
Application | HP | # of Belts | Hours / Year | Motor Eff. (estimated) | Tighten / Notched Belt Eff Improvement | kW Saving | kWh Saving | $ Saving | Marginal Cost
RAC-1 | 25 | 1 | 4380 | 89.5% | 2% | 0.41676 | 1825.4078 | 164.2867 | 15
RAC-2 | 25 | 1 | 4380 | 89.5% | 2% | 0.41676 | 1825.4078 | 164.2867 | 15
AC-2 | 5 | 2 | 4380 | 89.5% | 2% | 0.083352 | 365.0816 | 32.8573 | 30
Total |  | 4 |  |  |  | 0.91687 | 4015.8972 | 361.4307 | 73.8
|  |  | Total Energy Savings (KWh): | 4015.8972 |  |  | Total Implementation Cost: | 73.8
|  |  | Total Energy Savings ($): | 361.4307 |  |  | Simple Payback (years): | 0.20419
Description |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Standard B section V-belt 52" Grainger 1A097 |  |  | ea | 1 | 40 | 0 | 0 | 40 | 40
Cogged BX section V-belt 52" Grainger 13W530 |  |  | ea | 1 | 55 | 0 | 0 | 55 | 55
Marginal cost to upgrade |  |  | ea | 4 | 15 | 0 | 0 | 15 | 60
|  |  |  | Subtotal |  |  |  | 110 | 60
| Material cost allowance for hoses and clamps |  |  | Contingency |  |  |  | 0.08 | 4.8
|  |  |  | OH |  |  |  | 0.05 | 3
|  |  |  | Profit |  |  |  | 0.1 | 6
|  |  |  | Total |  |  |  |  | 73.8
| Source of performance data: |  | DOE/GO-102005-206 Motor Systems Tip Sheet #5. Indicating 2% increase in efficiency with
Gates white paper: Selecting the Right Drive System - Costs and Performance indicating same

## 12-DuctAirLoss
Reduce Duct Air Loss Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Assume duct is in an unconditioned space for worst case. For ducts in conditioned spaces divide energy losses by 1/3. To use input values for Width and Height of opening. Confirm VP, Run hours per day, HDD, CDD, grains of H2O entering, and grains of H2O leaving. Spreadsheet will calculate estimated BTUs and KWh wasted.
Formulas: | [7 empty] | cost per kW: |  | 0.09
Air Velocity (FPM) = 4005 x sqrt(Velocity Pressure (VP)) |  |  |  | Velocity Pressure (In. WC) |  |  | 0.1402 | Run hours /day |  | 12
CFM = Air Velocity (VA) x Area of opening (FT2) |  |  |  |  | Opening: | Width (in) | 2 | Height (in) |  | 4
Sensible Heat: BTUh = CFM x 1.08 x ∆T | [5 empty] | Annual Heating degrees days: | 4021 | An. Cooling degree days: |  | 580
Latent Heat: BTUh = CFM x 0.68 x ∆W (W = grains of water/lb) |  |  |  | Air Velocity (VA) |  | 1499.6038 | Opening(SF) | 0.055556 | CFM | 83.3113
BTUs/year cooling = CDDs x ((CFM x1.08)+ (CFM x 0.68 x ∆W)) x run hours/day (sensible and latent heat)
[5 empty] | note: well insulated buildings with efficient heating systems will result in lower run hours |  |  | Grains H2O/lb entering (W1) |  | 105
BTUs/year heating = HDDs x (CFM x1.08) x run hours/day | [7 empty] | Grains H2O/lb leaving (W2) |  | 40
Fan Horsepower = CFM x VP/ 6356 x fan efficiency | [8 empty] | ∆W | 65
1 HP = | 0.7457 | kW Fan Efficiency | 85%
Hours per day run x KW x 365 = KWh per year |  |  |  |  | 1 KWh = | 3412.1416 | BTU | 1 BTU = | 0.00029307 | KWh
Default VP of 0.1402 will provide a VA of 1500 average duct pressure. Default 105 grains H2O = 80 deg/70% rh; 40 grains H2O = 60 deg. 50% Rh. Default 12 hours run time
BTUs/year Heating: |  | 4341532.9033 | BTUs/year Cooling: |  | 26255462.9213 | Total BTUs/ year |  | 30596995.8246 | Fan KWh | 6.8417
For Ducts Running in Unconditioned Spaces
| Total yearly KWh used based on BTUs/ year |  |  | 8973.936 |  | Project cost from estimate worksheet |  |  | 1283.1975
| Cost of KW /yr required: |  |  | 807.6542 |  | Payback: |  |  | 1.5888
For Ducts Running in Conditioned Spaces
| Total yearly KWh used based on BTUs/ year |  |  | 2991.312 |  | Project cost from estimate worksheet |  |  | 1283.1975
| Cost of KW /yr required: |  |  | 269.2181 |  | Payback: |  |  | 4.7664
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Remove existing flex connect, clean, prepare for repair |  |  |  | ln. in. | 90 | 0.25 | 2 | 0.1 | 2.35 | 211.5
Add new duct material, pop rivet or screw to fasten |  |  |  | sq. in | 90 | 3 | 5 | 0.5 | 8.5 | 765
Apply duct mastic to seal tightly |  |  |  | sq. in | 8 | 2 | 3 | 0.1 | 5.1 | 40.8
replace duct insulation as required and tape |  |  |  | sq. in | 8 | 0.2 | 1 | 0.1 | 1.3 | 10.4
Clean up |  |  |  | na | 1 | 0.4 | 15 | 0.15 | 15.55 | 15.55
[5 empty] | Subtotal |  |  |  | 32.8 | 1043.25
[5 empty] | Contingency |  |  |  | 8% | 83.46
[5 empty] | OH |  |  |  | 5% | 52.1625
[5 empty] | Profit |  |  |  | 10% | 104.325
[5 empty] | Total |  |  |  |  | 1283.1975

## 13-DHWInsultation
Insulate Domestic Hot Water Piping Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Domestic Hot water piping in mechanical room is not insulated. There is a recirculation pump on the domestic hot water system. Heat is lost whenever pump is operating. Input hours provided in spreadsheet.
Conversion Factors: |  |  |  | Heat loss (BTUs/hour per foot)
1 deg F ∆T x 1 lb of water 1 |  | 1 | BTU | Pipe Diameter | Temperature difference |  |  | Uninsulated pipe (ft.) |  | 25
1 Gallon water = |  | 8.33 | lbs |  | 40o | 68o | 99o
1 BTU = |  | 1e-05 | Therms | 1/2" | 22 | 34 | 47 | Diameter of pipe (in.) |  | 3/4"
1 therm = |  | 100000 | BTUs | 3/4" | 29 | 45 | 64 |  | ∆T | 40
Coversion of KWh to BTU |  | 3412 |  | 1" | 36 | 56 | 79 | Heat Loss from table |  | 29
conversion of BTU to KWh: |  | 0.00029307 |  | 1-1/4" | 43 | 67 | 93
cost per kW: |  | 0.09 |  | 1-1/2" | 49 | 77 | 108 | Total BTU Loss/ hour |  | 725
cost per therm: |  | 0.8 |  | 2" | 62 | 97 | 136
http://www.engineeringtoolbox.com/copper-pipe-heat-loss-d_19.html |  |  |  | 2-1/2" | 74 | 116 | 162 | Hours /day operating |  | 24
|  |  |  | 3" | 87 | 135 | 189 | Days/ week operating |  | 7
Type of hot water source |  | electricity |  | 4" | 111 | 172 | 241 | Weeks per year |  | 52
Total BTUs lost per year |  | 6333600
Total kWh lost per year |  | 1856.1949 |  |  | KWh saved by insulating pipe: |  |  |  | 1856.1949
Total Therms lost per year |  | 63.336 |  |  | Cost of KW /yr saved: |  |  |  | 167.0575
Cost of kWh lost (electricity) |  | 167.0575 |  |  | Project cost from estimate worksheet |  |  |  | 271.35
Cost of therms lost (gas) |  | 50.6688 |  |  | Payback: |  |  |  | 1.6243 | Years
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Install new pipe insulation |  |  |  | ln ft. | 25 | 4 | 2.75 | 0.05 | 6.8 | 170
Clean up |  |  |  | na | 1 | 5 | 25 | 1 | 31 | 31
[5 empty] | Subtotal |  |  |  | 37.8 | 201
[5 empty] | Contingency |  |  |  | 15% | 30.15
[5 empty] | OH |  |  |  | 10% | 20.1
[5 empty] | Profit |  |  |  | 10% | 20.1
[5 empty] | Total |  |  |  |  | 271.35

## 14-ElectricBaseboard
Clean Electric Baseboard/Seasonal Lockout/Unoccupied Cutoff Payback
Building # |  | 1000 | Sample Building |  | Navy Base |  |  | Washington DC |  |  | 2023-01-01
Estimate assumes existing baseboard heaters are cleaned, seasonal lockout at circuit breaker or controls, and unoccupied cutoff. Note that heaters are supplemental for occupant comfort with main space conditioning by HVAC system. Assume new thermostats that allow control, and integration with building control system if possible. Note that cleaning is recommended yearly in October to remove summer build-up of dust using solvent, brushes, and vacuum.
| Watts per Linear Foot |  |  | 250 |  | Run months with no lockout |  |  |  |  | 8
| Linear Feet of Baseboard |  |  | 64 |  | Run months with seasonal lockout |  |  |  |  | 6
| Total Wattage |  |  | 16000 |  | Average days per month |  |  |  |  | 30
| Efficiency when clean |  |  | 100% |  | Estimated average run time percentage |  |  |  |  | 50%
| Efficiency when dirty |  |  | 75% |  | Hours run time per day no unoccupied cutoff |  |  |  |  | 24
| Electric Rate / KWh |  |  | 0.09 |  | Hours run time per day w/ unoccupied cutoff |  |  |  |  | 14
| Conversion KWh to BTUs |  |  | 3412 |  | Formula: KWh per year = (Wattage x (1/efficency) x months x days per month x run time percentage x hours run per day)/ 1000 watts per KW
| Est. current KWh use per year |  | 61440 | 5529.6 |  | Estimated KWh use after cleaning w/ lockout |  |  |  | 34560 | 3110.4
| Est. KWh per year with cleaning |  | 46080 | 4147.2 |  | KWh use after cleaning, lockout, unoc. cutoff |  |  |  | 20160 | 1814.4
| Savings with Cleaning |  | 15360 | 1382.4 |  | Total Savings with all recomendations |  |  |  | 41280 | 3715.2
| Sources: | https://inspectapedia.com/heat/Electric_Baseboard_Heat_Length.php |  |  |  |  | https://www.doityourself.com/forum/heat-pumps-electric-home-heating/330253-electric-baseboard-heater-run-time.html
| https://forums.jlconline.com/forums/forum/jlc-online-expert-forums/the-electric-shop/56686-how-to-calculate-the-energy-cost-for-electric-baseboard-heat | [5 empty] | cadetheat.com/blog/how-much-does-it-cost-to-run-my-heater/ |  |  | https://michaelbluejay.com/electricity/heating-questions.html
|  | Energy Saved |  |  | 41280 |  | Cost from estimate worksheet |  |  | 5477.22
|  | Cost of energy saved per year: |  |  | 3715.2 |  | Payback (years) |  |  | 1.4743
| Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
| Clean baseboard fins with solvent, brushes, vacuum |  |  |  | ln ft. | 64 | 0.2 | 2 | 0.1 | 2.3 | 147.2
| Install "smart" thermostats and tie to control system if possible |  |  |  | ea | 3 | 350 | 500 | 15 | 865 | 2595
| Seasonal lockout |  |  |  | ea | 1 | 250 | 300 | 15 | 565 | 565
| Unoccupied Setback |  |  |  | ea | 1 | 250 | 300 | 15 | 565 | 565
| Clean up |  |  |  | ea | 1 | 20 | 150 | 15 | 185 | 185
[6 empty] | Subtotal |  |  |  | 2182.3 | 4057.2
[6 empty] | Contingency |  |  |  | 15% | 608.58
[6 empty] | OH |  |  |  | 10% | 405.72
[6 empty] | Profit |  |  |  | 10% | 405.72
[6 empty] | Total |  |  |  |  | 5477.22

## 15-MotionSensor
Bathroom Motion Sensor Addition for Fan and Lights Payback
Building # | 1000 | Sample Building |  |  |  | Navy Base |  |  |  | Washington DC |  |  |  | 2023-01-01
Assume that the Exhaust Fan and Toilet Room lights are left on 1/3 of the day = 8 hours. With Motion Sensor assume 2 hours. Energy loss from fans come from both electricity used and CFMs of conditioned air lost to the exterior | [10 empty] | Electric Rate ($ per KWh): |  |  | 0.09
[11 empty] | Thermal Rate ($ per MBtu): |  |  | 8
Location |  | Device Properties |  |  |  |  | Quantity and Use |  |  |  | Energy Savings |  |  | Replace
|  | Type | Watts | Initial Lumens | Service Life (hours) | Device Cost | Quantity | hours/ day | days/ week | weeks | KW hours | KWh saved | Annual KWh Cost Savings | Annual Replacement Cost
Toilet Room | Existing | T-8 | 28 | 2800 | 28000 | 2 | 6 | 8 | 7 | 52 | 489.216 | 366.912 | 33.0221 | 1.248
| Proposed | T-8 | 28 | 2800 | 28000 | 2 | 6 | 2 | 7 | 52 | 122.304 |  |  | 0.312
Toilet Room | Existing | Ex Fan | 90 | 0 | 15000 | 150 | 1 | 8 | 7 | 52 | 262.08 | 196.56 | 17.6904 | 29.12
| Proposed | Ex Fan | 90 | 0 | 15000 | 150 | 1 | 2 | 7 | 52 | 65.52 |  |  | 7.28
Measured CFM rate for each Exhaust Fan was 180 CFM model Typical efficiency of 2 CFM per Watt = 90 Watts. | [7 empty] | Total Savings |  |  |  | Annual KWh Saved | Annual KWh Cost | Annual Rep. Cost savings
[12 empty] | 563.472 | 50.7125 | 22.776
Replacement Cost Savings: |  |  | Replacement $ = Quantity of devices x cost per item x hours / service life
Energy Loss From Conditioned Air Exhausted by Fan
Heating Degree Days: |  | 4988 | Basic Formula for Fan in continuous use: BTU = Fan CFM x HDD or CCD x 60 min. x 24 hours x specific heat of air
Cooling Degree Days: |  | 582 | Source: www.degreedays.net (temperature data from www.wunderground.com) National Airport |  |  |  |  | Btu/hr to KWh: |  |  |  |  | 0.00029307
Exhaust Fan CFM: |  | 180 | [5 empty] | Specific Heat of Air |  |  |  |  | 0.018
Cooling COP |  | 3 | This calculation assumes that either the air infiltration into the zone served or the HVAC system ventilation air increases when this exhaust fan is operating
Heating COP |  | 0.85
|  |  |  | Continuous Fan Operation (24/7) |  | 8 Hour Operation (24 hr. / 3) |  | 2 Hour Operation (8 hr. / 4) |  |  | Ventilation Load Energy Savings
|  |  | Ventilation Heating Load (Btu): | 23272012.8 |  | 7757337.6 |  | 1939334.4 |  |  | 5818003.2 |  | Btu
|  |  | Ventilation Cooling Load (Btu): | 2715379.2 |  | 905126.4 |  | 226281.6 |  |  | 678844.8 |  | Btu
|  |  | Heating Energy (MBtu): | 27.3788 |  | 9.1263 |  | 2.2816 |  |  | 6.8447 |  | MBtu
|  |  | Cooling Energy (kWh): | 265.2664 |  | 88.4221 |  | 22.1055 |  |  | 66.3166 |  | kWh
|  |  | Total Energy Cost: | 243.8862 |  | 81.2954 |  | 20.3238 |  |  | 60.7262
|  |  |  | Total Electrical Energy Savings (KWh) | 629.7886 | kWh | [5 empty] | Total Implementation Cost | 741.69
|  |  |  | Total Thermal Energy Savings (MBtu) | 6.8447 | MBtu | [5 empty] | Simple Payback | 5.5261 | years
|  |  |  | Total Energy and Replacement Cost Savings ($) | 134.2147
| Description |  |  |  |  | unit | QTY | material |  | labor |  | Equip. | Per unit | Total
| Install HSRS (assume 1 per 4 switches) |  |  |  |  | ea | 1 | 350 |  | 250 |  | 3 | 603 | 603
[6 empty] | ea | 0 | 0 |  | 0 |  | 0 | 0 | 0
[9 empty] | Subtotal |  |  |  | 603 | 603
|  | Number of Toilet Room Fan/ lights to replace: |  |  |  | 1 |  |  | Contingency |  |  |  | 8% | 48.24
[9 empty] | OH |  |  |  | 5% | 30.15
[9 empty] | Profit |  |  |  | 10% | 60.3
[9 empty] | Total |  |  |  |  | 741.69

## 16-HHWValve
Repair Non-Closing HHW Valve on Coil Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
HHW valve does not close fully on the duct reheat coil serving the South side of the Weight Room. HHW flow in the coil will cause heat transfer whenever fan is on, using energy from the HHW system. Additionally, electrical cooling energy (DX) will be needed to offset the heating energy induced by the HHW system.
Airside Btu Calculation: U=1.08*CFM*DeltaT
| Cooling COP: | 3 |  |  | Supply Air CFM: | 1400 | CFM | Cost per kWh: | 0.09 | $/kWh
| Heating COP: | 0.85 |  |  | HHW Coil Airside DeltaT: | 40 | °F | Cost per Mbtu: | 8 | $/MBtu
| Valve stuck position: | 10% |  |  | HHW coil design capacity: | 60480 | Btu/hr
Assumptions: | [7 empty] | Heating energy used when fan is operating: | 6048 | Btu/hr
1) AH operates 100% of the time during occupied hours (M-F 0500-2000, SS 0900-1700). 2) HHW valve has negligible impact when fan is not operating. 3) HHW valve is called to be fully closed during full cooling hours. 4) Four "Cooling" months per year, when reheat is not needed. 5) Electrical cooling energy used to offset excess HHW use is essentially equal. | [7 empty] | Electrical cooling energy used to offset excess HHW use: | 6048 | Btu/hr
[8 empty] | AHU operating hours: | 1698.6667 | hours
[8 empty] | Excess HHW energy used when fan is operating: | 12.0865 | Mbtu
[8 empty] | HHW energy cost: | 113.7554
[8 empty] | Electrical cooling energy used to offset excess Heating use: | 10.2735 | Mbtu
[8 empty] | Electrical cooling energy used to offset excess Heating use: | 1003.6671 | kWh
[8 empty] | Electrical cooling energy cost: | 90.33
[8 empty] | Total cost of HHW valve being stuck partially open: | 204.0855
| Heating Energy Savings: | 12.0865 | MBtu
| Cooling Energy Savings: | 1003.6671 | kWh |  |  |  |  | Implementation Cost: | 1035.66
| Energy Cost Savings: | 204.0855 | [5 empty] | Simple Payback: | 5.0746 | years
Division # | Description |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
23 09 53 10 | 3/4" Three-way valve |  |  | ea | 1 | 725 | 40 | 1 | 766 | 766
| Demo Old Valve |  |  | ea | 1 | 0 | 75 | 1 | 76 | 76
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Subtotal |  |  |  | 842 | 842
[5 empty] | Contingency |  |  |  | 8% | 67.36
[5 empty] | OH |  |  |  | 5% | 42.1
[5 empty] | Profit |  |  |  | 10% | 84.2
[5 empty] | Total |  |  |  |  | 1035.66
Note on H7: mbryan1: Based on 400 cfm/ton
Note on H9: mbryan1: Per design drawings

## 17-CHWValve
Repair Non-Closing CHW Valve on Coil Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
CHW valve does not close fully on AHU cooling coil serving South Offices. CHW flow in the coil will cause heat transfer whenever fan is on, using energy from the CHW system. Additionally, heating energy (HHW) will be needed to offset the excess cooling energy induced by the CHW system.
Airside Btu Calculation: U=1.08*CFM*DeltaT
| Cooling COP: | 3 |  | Supply Air CFM: | 1400 | CFM | Cost per kWh: | 0.09 | $/kWh
| Heating COP: | 0.85 |  | CHW Coil Airside DeltaT: | 30 | °F | Cost per Mbtu: | 8 | $/MBtu
| Valve stuck position: | 10% |  | CHW coil design capacity: | 45360 | Btu/hr
Assumptions: | [6 empty] | Cooling energy used when fan is operating: | 4536 | Btu/hr
1) AH operates 100% of the time during occupied hours (M-F 0500-2000, SS 0900-1700). 2) CHW valve has negligible impact when fan is not operating. 3) CHW valve is called to be fully closed during full heating hours. 4) Four "Heating" months per year, when cooling is not needed. 5) HHW heating energy used to offset excess CHW use is essentially equal. | [6 empty] | Heating energy used to offset excess cooling: | 4536 | Btu/hr
[7 empty] | AHU operating hours: | 1698.6667 | hours
[7 empty] | Cooling energy used when fan is operating: | 7.7052 | Mbtu
[7 empty] | Electrical cooling energy used when fan is operating: | 752.7503 | kWh
[7 empty] | CHW energy cost: | 72.5191
[7 empty] | HHW heating energy used to offset excess cooling: | 9.0649 | Mbtu
[7 empty] | Electrical cooling energy cost: | 72.5191
[7 empty] | Total cost of HHW valve being stuck partially open: | 145.0382
| Cooling Energy Savings: | 752.7503 | kWh
| Heating Energy Savings: | 9.0649 | MBtu |  |  |  | Implementation Cost: | 1035.66
| Energy Cost Savings: | 145.0382 |  |  |  |  | Simple Payback: | 7.1406 | years
Division # | Description |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
23 09 53 10 | 3/4" Three-way valve |  |  | ea | 1 | 725 | 40 | 1 | 766 | 766
| Demo Old Valve |  |  | ea | 1 | 0 | 75 | 1 | 76 | 76
[5 empty] | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Subtotal |  |  |  | 842 | 842
[5 empty] | Contingency |  |  |  | 8% | 67.36
[5 empty] | OH |  |  |  | 5% | 42.1
[5 empty] | Profit |  |  |  | 10% | 84.2
[5 empty] | Total |  |  |  |  | 1035.66
Note on G7: mbryan1: Based on 400 cfm/ton
Note on G9: mbryan1: Per design drawings

## 18-WindowUnits
Replace Window Type Units With Mini Split Ductless Units Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Air Infiltration Heat and Cooling Loss Calculations:
Assume the openings around the window type unit ac to total .005sq. ft.
Infiltration: | V = I x A |  |  |  | area of each opening |  |  |  | 0.01 | sq feet
V = ventilation air in CFM |  |  |  |  | Total number of openings requiring attention: |  |  |  |  | 4
I = Infiltration rate (cfm/sq ft)* = |  |  | 1.5 |  | V (CFM) = | 0.06
A = area of cracks/ openings in sq ft. |  |  |  |  | Annual Heating degrees days: |  |  |  | 4021
heat capacity of air (Btu/ CFt.)= |  |  | 0.018 |  | Annual Cooling degree days: |  |  |  | 580
Q = .018 x V x temp dif.
Qyr = .018 x cubic ft. /day x degree days
coversion of Btu/hr to KW: |  | 0.00029307 |  |  | KWh required for BTUs/ year |  |  |  | 765.4279
cost per kW: |  | 0.09 |  |  | Cost of KW /yr required: |  |  |  | 68.8885
[5 empty] | Project cost from estimate worksheet |  |  |  | 16733.412
BTU heating loss |  | 6253.4592 |  |  | Payback: |  |  |  | 242.9057 | Years
BTU cooling loss |  | 902.016
Total BTUs (Q/day) |  | 7155.4752 | (Extra BTUs heating and cooling required per day)
BTUs per year: |  | 2611748.448
*http://ibpsa-boston.com/minutes/IBPSAboston-presentations_2011-09-16_Gowri.pdf
http://www.cedengineering.com/upload/Heat%20Loss%20Calculations%20and%20Principles.pdf
Existing window units to be removed and replaced with modern mini-split heat pump units of high efficiency that meet current codes.
Savings from installing higher efficiency air conditioning equipment
Room Width | 12 | Room Length | 16 | Wall Height (ft) | 10 | Calculated Surface area (Room area x exterior wall) |  | 1920 | Average U value | 0.2
Q = A x U x (Ti - To) |  |  | Number of rooms |  | 2 |  |  | Estimated internal load density: | 180 | Btu/hr-sf
Q = Total hourly rate of heat loss | [7 empty] | Daily internal load schedule: | 24 | hrs/day
U = overall heat transfer coef. Btu/hr sq ft | [7 empty] | Weekly internal load schedule: | 7 | days/week
A = Net area | [7 empty] | Annual internal load schedule (cooling season): | 40 | weeks/year
Ti = Inside design temp | [7 empty] | Estimated internal load (for cooling only): | 464486400 | Btu
To = Outside design temp
BTUs per year = (U value x surface area x CDD x 24 ) + internal load)/ COP
[6 empty] | Estimated BTUs used by existing Window Unit: |  |  |  | 187932672
COP of existing Window AC Unit: |  |  | 2.5 |  |  | Estimated BTUs used by mini-split Unit: |  |  |  | 72281796.9231
COP of VRF Mini Split Ductless Unit: |  |  | 6.5 |  |  | Estimated BTUs saved by replacing existing unit: |  |  |  | 115650875.0769
| Energy Saved |  |  | 33893.9257 | KWh | Cost from estimate worksheet |  |  | 16733.412
| Cost of energy saved per year: |  |  | 3050.4533 |  | Payback (years) |  |  | 5.4855
| Total Energy Saved |  |  | 34659.3536 | KWh | Cost from estimate worksheet |  |  | 16733.412
| Total Cost of energy saved per year: |  |  | 3119.3418 |  | Payback (years) |  |  | 5.3644
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Remove existing window unit and seal opening |  |  |  | ea | 4 | 2 | 230 | 1 | 233 | 932
Install new Ductless Split Unit |  |  |  | ea | 2 | 3800 | 2500 | 35 | 6335 | 12670
Clean up |  |  |  | na | 2 | 0.4 | 0.4 | 0.4 | 1.2 | 2.4
[5 empty] | Subtotal |  |  |  | 6569.2 | 13604.4
[5 empty] | Contingency |  |  |  | 8% | 1088.352
[5 empty] | OH |  |  |  | 5% | 680.22
[5 empty] | Profit |  |  |  | 10% | 1360.44
[5 empty] | Total |  |  |  |  | 16733.412

## 19-CompAirLeaks
Repair Compressed Air Leaks Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  | 2023-01-01
Four (4) audible air leaks were discovered during the survey.
Basic Equation |  | K = LR x E x UR x hr |  |  |  | Energy Rate | 0.09 | $/kWh
K= | kW Saved
LR= | Leakage Rate |  |  |  |  | Days per Week | 5
h= | Operating Hours |  |  |  |  | Hours per Day | 12
E= | Energy to compress air |  | 0.18 | kW/CFM |  | Weeks per Year | 52
source: Kaeser Compressors
Summary Table
| Orifice Size (in) | Operating Pressure (psig) | LR (CFM) (from table) | Number | Hours / Year | kWh | Cost Savings
| 1/32 | 100 | 1.62 | 1 | 3120 | 909.792 | 81.8813
| 1/16 | 100 | 6.5 | 1 | 3120 | 3650.4 | 328.536
| 1/8 | 100 | 26 | 2 | 3120 | 29203.2 | 2628.288
[5 empty] | SUM | 33763.392 | 3038.7053
|  | Total Energy Savings (KWh) | 33763.392 |  |  | Total Implementation Cost | 1476.492
|  | Total Energy Cost Savings ($) | 3038.7053 |  |  | Simple Payback (years) | 0.4859
source: Sullair Corporation
Description |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Repair Leaks |  |  | ea | 4 | 150 | 150 | 0.1 | 300.1 | 1200.4
|  |  |  | Subtotal |  |  |  | 300.1 | 1200.4
| Material cost allowance for hoses and clamps |  |  | Contingency |  |  |  | 0.08 | 96.032
|  |  |  | OH |  |  |  | 0.05 | 60.02
|  |  |  | Profit |  |  |  | 0.1 | 120.04
|  |  |  | Total |  |  |  |  | 1476.492

## 20-DestratFans
Add Destratification Fans Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  |  | Washington DC |  |  | 2023-01-01
High ceiling temperatures observed in high bay area. Install destratification fans to assist in maintaining even heated air distribution and prevent stratification. Design Basis: Airius, Air Pear. Assume approx 5000sf/fan | [8 empty] | Electric Rate ($ per kWh): |  | 0.09
[9 empty] | Thermal Rate ($ per MBtu): |  | 8
| Heat Loss: | Q = Hrs x A x U x (Tc - Tz)
|  | Q = Total excess heat loss, Btu |  |  |  |  | Net Roof Area: |  |  | 1800 | sq ft
|  | Hrs = Total Heating season hours |  |  |  |  | Estimated Roof U-value: |  |  | 0.2 | (approx. R-5)
|  | U = overall heat transfer coef. Btu/hr sq ft |  |  |  |  | Zone heating setpoint: |  |  | 65 | °F
|  | A = Net area |  |  |  |  | Measured Ceiling Temperature: |  |  | 73 | °F
Tc = Temperature of ceiling of heated zone
|  | Tz = Design zone temperature setpoint |  |  |  |  | Approximate heating season hours: |  |  | 5840 | hours
| Convert: | 1 Btu = | 0.00029307 | kWh |  |  | Heating COP: |  |  | 0.85
| Excess heat loss through roof due to stratification: |  |  |  | 19787294.1176 | Btu | Approximate fan power: |  |  | 45 | watts
| Electrical Energy Use: |  |  |  | 262.8 | kWh | Number of destrat fans: |  |  | 1
|  |  |  | Total Energy Savings (MBtu) | 19.7873 | MBtu
|  |  |  | Total Energy Cost (kWh) | 262.8 | kWh |  |  | Total Implementation Cost | 3763.8
|  |  |  | Total Energy Cost Savings ($) | 134.6464 |  |  |  | Simple Payback (years) | 27.9532 | years
Division # | Description |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
| Prep and Hanger installation |  |  | ea | 1 | 75 | 150 | 2 | 227 | 227
| Electrical Conduit and Switch for fans |  |  | ea | 1 | 60 | 450 | 7 | 517 | 517
| Install new destrat fans |  |  | ea | 1 | 1400 | 600 | 75 | 2075 | 2075
| Install new destrat fans |  |  | ea | 1 | 35 | 200 | 6 | 241 | 241
[5 empty] | Subtotal |  |  |  | 3060 | 3060
|  | Design Basis: Air Pear by Airius Corporation |  |  | Contingency |  |  |  | 8% | 244.8
[5 empty] | OH |  |  |  | 5% | 153
[5 empty] | Profit |  |  |  | 10% | 306
[5 empty] | Total |  |  |  |  | 3763.8

## 21-LSCeilingFan
Add Low Speed Ceiling Fan Payback
Building # | 1000 | Sample Building |  |  |  | Navy Base |  |  |  | Washington DC |  |  | 2023-01-01
Calculation is based on replacing the existing 12 standard ceiling fans with 1 - 14' low-speed industrial ceiling fan. Example is from a gym aerobics room where the moving air dramatically increases comfort without lowering thermostat which would use more energy. | [10 empty] | Electric Rate ($ per KWh): |  |  | 0.09
KWh = Watts x hours/ 1000
Annual savings = Rate x KWh
Location |  | Device Properties |  |  |  |  | Quantity and Use |  |  |  | Energy Savings |  |  | Replace
|  | Type | Watts | Initial Lumens | Service Life (hours) | Device Cost | Quantity | hours/ day | days/ week | weeks | KW hours | KWh saved | Annual KWh Cost Savings | Annual Replacement Cost
Crossfit Room | Existing | Standard Ceiling fans | 200 | na | 10000 | 550 | 12 | 16 | 7 | 40 | 10752 | 9766.4 | 878.976 | 2956.8
| Proposed | Low speed ceiling fan | 220 | na | 10000 | 3800 | 1 | 16 | 7 | 40 | 985.6 |  |  | 1702.4
http://www.homedepot.com/catalog/pdfImages/56/56d8c607-dce5-4c39-a7da-dd422f81eb3d.pdf ; http://www.bigassfans.com/onlineguides/isis/Isis-Install-Guide-Online.pdf | [7 empty] | Total Savings |  |  |  | Annual KWh Saved | Annual KWh Cost | An. Rep. Cost sav.
[12 empty] | 9766.4 | 878.976 | 1254.4
Replacement Cost Savings: |  |  | Replacement $ = Quantity of devices x cost per item x hours / service life
Formula for Amps of motor : Amps = HP x 746/ Voltage x Efficiency x Power Factor x 2 (single phase) | [11 empty] | Watts = Amps x Volts
HP: | 0.75 | Voltage: | 110 | Effic. | 0.9 | P. F. | 0.75 |  | Amps: |  | 6.8666 |  | Watts: | 755.325
Proposed Ceiling Fan Amps at 50% speed (from manufactures Literature - full load = 3.9): | [10 empty] | 2 |  | Watts: | 220
De - stratification of heat in winter - Delta T between exterior and interior calculation at roof
With de-stratification the warm air will not stay stagnant at the ceiling, and thus the Delta T will be less between interior and exterior
Basic Heat loss Formula | Q = A x U x (Ti - To) | [5 empty] | Estimated Roof U value: |  |  |  | 0.21 |  | U Value
| Q = Total hourly rate of heat loss | [5 empty] | Net Area: |  |  |  | 2500 |  | sq. ft.
| U = overall heat transfer coef. Btu/hr sq ft |  |  |  |  | Multiply hourly rate of heat loss by 24 for 243 day heating season
A = Net area
| Ti = Inside design temp |  |  |  |  | Total yearly Heat Loss with fan |  |  |  |  | 62762705.7534 |  | BTUs
| To = Outside design temp |  |  |  |  | Total yearly Heat Loss without fan |  |  |  |  | 74530713.0822 |  | BTUs
Heating Degrees Days @ 68 deg. F: |  |  | 4988 | [5 empty] | Savings: |  | 11768007.3288 |  | BTUs
Average Degree day Temperature difference during heating season (HDD/(2/3 *365) |  |  | 20.4986 |  | Average Temperature difference with air stratification - heat rises to ceiling |  |  |  |  | 28.5 | 3448.8625 |  | KWh
With Ceiling fan assume 20.5 Degree Delta T, with out fan assume 28.5 degrees Delta T | [10 empty] | 310.3976
Convert BTUs to KWh: 1 BTU/hr = 0.00029307107 kW
Implementation Cost
Description of work | [5 empty] | Total items | Labor Cost per hour |  | Labor hours/ item |  | Material cost/item | Equip. Cost /item | Total Cost
Remove existing ceiling fans and cap junction boxes | [5 empty] | 1 | 70 |  | 2 |  | 12 | 1 | 153
Prep work and hanger installation | [5 empty] | 1 | 70 |  | 2 |  | 12 | 1 | 153
Add electrical conduit and switch for fan | [5 empty] | 1 | 70 |  | 3 |  | 40 | 5 | 255
Install new Big Ass Fans Model 4900 (includes lift rental) | [5 empty] | 1 | 70 |  | 6 |  | 3800 | 500 | 4720
Clean up | [5 empty] | 1 | 25 |  | 4 |  | 25 | 4 | 129
[10 empty] | SUBTOTAL |  |  | 5410
[10 empty] | OVERHEAD (5%) |  |  | 270.5
[10 empty] | PROFIT (10%) |  |  | 27.05
Total Energy Savings (KWh) |  |  |  | 13215.2625 |  |  | Total Implementation Cost | [5 empty] | 5707.55
Total Energy Savings ($) |  |  |  | 2443.7736 |  |  | Payback (years) | [5 empty] | 1.5433
Note on B31: Boyd, Andrew F CIV NAVFAC Washington:
Note on B32: Boyd, Andrew F CIV NAVFAC Washington:
Note on B33: Boyd, Andrew F CIV NAVFAC Washington:
Note on B34: Boyd, Andrew F CIV NAVFAC Washington:
Note on B35: Boyd, Andrew F CIV NAVFAC Washington:

## 22-HSRSWindows
Add HVAC Smart Relay Switch (HSRS) to Windows Payback
Building # | 1000 | Sample Building |  | Navy Base |  | Washington DC |  |  | 2023-01-01
HSRS switches turn off HVAC system / Fan Coils in rooms when occupants open windows. Available in Wired or Wireless versions. Typically each HSRS can support 4 wired or 8 wireless reed switch sensors.
Infiltration: | V = I x A |  | 3' wide window opened 15" high bottom sash |  |  |  |  | 3.25 | sq feet
V = ventilarion air in CFM |  |  | number of windows requiring attention (1/2 open): |  |  |  |  | 64
I = Infiltration rate (assume 0.15 cfm/sq ft)* |  |  | V (CFM) = | 31.2
A = area of cracks/ openings in sq ft. |  |  | Annual Heating degrees days: |  |  | 3877 | 387.7 | assume 10% time open
.018 = heat capacity of air Btu/ cubic foot |  |  | Annual Cooling degree days: |  |  | 1564 | 156.4 | assume 10% time open
Q = .018 x V x temp dif. |  |  | Extra BTUs heating and cooling required: |  |  |  | 440015.8464
Qyr = .018 x cubic ft. /day x degree days |  |  | KW required for BTUs/ year |  |  |  | 47068.9089
coversion of Btu/hr to KW: |  | 0.00029307 | Cost of KW /yr required: |  |  |  | 4236.2018
cost per kW: |  | 0.09 | Project cost from estimate worksheet |  |  |  | 13112.784
313534.5408 | BTU heating loss |  | Payback: |  |  |  | 3.0954 | Years
126481.3056 | BTU cooling loss
* http://www.cedengineering.com/upload/Heat%20Loss%20Calculations%20and%20Principles.pdf
Description |  |  |  | unit | QTY | material | labor | Equip. | Per unit | Total
Install HSRS (assume 1 per 4 switches) |  |  |  | ea | 8 | 350 | 120 | 3 | 473 | 3784
Install Reed switches at each window |  |  |  | ea | 64 | 30 | 45 | 1 | 76 | 4864
Misc. Wiring of switches and window weatherstripping prep. |  |  |  | ea | 64 | 3 | 15 | 1 | 19 | 1216
Programming the controllers |  |  |  | ea | 8 | 15 | 75 | 2 | 92 | 736
Clean up |  |  |  | ea | 64 | 0.4 | 0.5 | 0.05 | 0.95 | 60.8
[5 empty] | Subtotal |  |  |  | 660.95 | 10660.8
[5 empty] | Contingency |  |  |  | 8% | 852.864
[5 empty] | OH |  |  |  | 5% | 533.04
[5 empty] | Profit |  |  |  | 10% | 1066.08
[5 empty] | Total |  |  |  |  | 13112.784

## 23-HeatShrinkWindows
Add Heat Shrink Plastic Film to Windows Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  |  | Washington DC |  |  | 2023-01-01
R-Value Upgrade Calculations
Project assumes a 2 man crew with ladders removing ceiling tiles at each window, applying heat shrink plastic film, replacing tiles, and cleaning up. Work would likely be done in sections, likely evenings and weekends to avoid disrupting occupants during work hours. | [5 empty] | 90 |  | SF |  | Cost Per KWh | 0.09
[5 empty] | Existing: | Air film |  | R | 0.5 | Existing Heating loss
Heat loss |  | Q = A x U x (Ti - To) |  |  |  | Exterior Gypsum Board |  | R | 1 | Q: Btu/ hr | 104.3663
Q = Total hourly rate of heat loss | [5 empty] | Batt insulation (assumed) |  | R | 15 | Existing Cooling loss
U = overall heat transfer coef. Btu/hr sq ft | [5 empty] | Themal bridging ded. |  | R | -7 | Q: Btu/ hr | 18.6878
A = Net area | [5 empty] | Total R value |  |  | 9.5 | Reduced Heating Loss
Ti = Inside design temp | [9 empty] | Q: Btu/ hr | 42.1906
To = Outside design temp | [9 empty] | Reduced Cooling Loss
1 KWh = 3412.14 BTU |  |  |  |  | Proposed: | Total from above |  | R | 9.5 | Q: Btu/ hr | 7.5546
1 BTU/hr = 0.00029307107 kWh | [7 empty] | R
Annual Heating degrees days: |  |  | 4021 |  |  | Increased Batt insul |  | R | 9 | Total KW per hour saved
Annual Cooling degree days: (no cooling) |  |  | 720 |  |  | continuous insulation |  | R | 5 |  | 0.021485
Average Daily To heating = HDD/365 |  |  | 11.0164 | [6 empty] | Total KWh per year saved
Average Daily To cooling = CDD/365 |  |  | 1.9726 |  |  | Total R value |  |  | 23.5 |  | 188.2059
Heating savings Btu/ hour with insulation: |  |  |  |  | 62.1756 |  |  |  |  | Cost of KWh Saved:
Cooling savings Btu / hour with insulation |  |  |  |  | 11.1332 | [5 empty] | 16.9385
Total savings Btu / hour with insulation |  |  |  |  | 73.3088 |  |  |  |  | Simple payback (years):
Total savings per year (avg/hour x 24 x 365) |  |  |  |  | 642185.1736 | BTUs |  |  |  |  | 456.2432
Air Infiltration Heat and Cooling Loss Calculations:
Currently there are gaps around the lights and perimeter, and a seam which has opened.
Infiltration: |  | V = I x A |  |  |  | Area of gap per linear foot |  |  |  | 0.012 | sq feet
V = ventilation air in CFM | [5 empty] | Total linear feet of gap |  |  |  |  | 35
I = Infiltration rate (cfm/sq ft)* = |  |  | 1.5 |  |  | V (CFM) = |  | 0.63
A = area of cracks/ openings in sq ft. |  |  | 0.42 |  |  | Annual Heating degrees days: |  |  |  | 4021
heat capacity of air (Btu/ CFt.)= |  |  | 0.018 |  |  | Annual Cooling degree days: |  |  |  | 720
Q = .018 x V x temp dif.
Qyr = .018 x cubic ft. /day x degree days
coversion of Btu/hr to KW: |  |  | 0.00029307 |  |  | KWh required for BTUs/ year |  |  |  | 8281.5441
cost per kW: |  |  | 0.09 |  |  | Cost of KW /yr required: |  |  |  | 745.339
[6 empty] | Project cost from estimate worksheet |  |  |  | 7728.09
BTU heating loss |  |  | 65661.3216 |  |  | Payback: |  |  |  | 10.3686 | Years
BTU cooling loss |  |  | 11757.312
Total BTUs (Q/ day) |  |  | 77418.6336 | (Extra BTUs heating and cooling required)
BTUs per year: |  |  | 28257801.264
*http://ibpsa-boston.com/minutes/IBPSAboston-presentations_2011-09-16_Gowri.pdf
http://www.cedengineering.com/upload/Heat%20Loss%20Calculations%20and%20Principles.pdf
Total Energy Savings (KWh) |  |  |  | 8469.7499 |  | Total Implementation Cost |  |  |  | 7728.09
Total Energy Savings ($) |  |  |  | 762.2775 |  | Payback (years) |  |  |  | 10.1382
Description |  |  | unit |  | QTY | material per unit | labor per unit |  | Equipment Per Unit | total per unit | Total
Remove existing ceiling, lights, and framing |  |  | square feet |  | 90 | 1.5 | 15 |  | 0.5 | 17 | 1530
Install new framing, R-19 Batt insulation, and continous foam board insulation. Air seal at perimeters with spray foam as needed |  |  | square feet |  | 140 | 6.25 | 14 |  | 2 | 22.25 | 3115
Install new exterior gypsum board ceiling, finsh, and paint |  |  | square feet |  | 140 | 1.5 | 5 |  | 0.5 | 7 | 980
Wire and install new LED cove lighting along perimeter of side walls and wall above door |  |  | linear foot |  | 28 | 17 | 6 |  | 0.5 | 23.5 | 658
[7 empty] | Subtotal |  |  | 39.25 | 6283
[7 empty] | Contingency |  |  | 8% | 502.64
[7 empty] | OH |  |  | 5% | 314.15
[7 empty] | Profit |  |  | 10% | 628.3
[7 empty] | Total |  |  |  | 7728.09

## 24-CleanGlass
Clean Glass Block/Daylighting Windows Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  | 2023-01-01
Building has visibly dirty glass block or windows used for daylighting. This will require more artificial light to be used which uses electricity and adds additional cooling load to HVAC system. (source: http://buildequinox.com/projects/equinox-house/features-and-tech/lighting-daylight/ )
Difuse sky radiation is approximately 150 Watts/ sq meter. |  |  |  |  | Transmittance through clean Glass Block approximately 50%
Vertical windows "see" approx. 50% of light - 75 Watts/sq. meter |  |  |  |  | Transmittance through clean Glass Block approx. 38 watts/sq. meter
Sunlight has approx 110 Lumens/ watt |  |  |  |  | 38 watts x 110 lumens = 4180 lumens/sq. meter
approximately 1800 sq. ft of glass block each side = 3600 total |  |  |  |  | 1 sq.ft = .093 sq. meter |  |  | 3600 x .093 = 335 sq. meters
Base Electric Rate ($/KWh) |  |  | 0.09
Condition | Quantity | Watts | Initial Lumens | hours/ day | days/ week | weeks | KW hours | KWh lost | Annual Savings
Clean Glass Block | 335 | 38 | 36850 | 8 | 7 | 50 | 35644 | 10693.2 | 962.388
Dirty Glass Block (30% reduction in lumens | 335 | 26.6 | 25795 | 8 | 7 | 50 | 24950.8
Payback: | 2.4951 | years |  | Cost: | 2401.245 |  | Cost of action/ savings = payback
Cost Estimate
Surface area of Glass Block to be cleaned | 1800
Description | Crew | Labor Hours | Unit | QTY (SF) | Material per unit | Labor per unit | Equip. per unit | total per unit | Total
Clean exterior of windows from ladders on low roofs | 4 | 8 | sf | 3600 | 0.02 | 0.26 | 0 | 0.28 | 1008
Clean interior of windows from mobile lift | 3 | 8 | sf | 3600 | 0.02 | 0.22 | 0.03 | 0.27 | 972
Subtotal | [8 empty] | 1980
OH | [5 empty] | 5% |  |  | 2079
Profit | [5 empty] | 10% |  |  | 2286.9
Contingency | [5 empty] | 5% |  |  | 2401.245
Total | [8 empty] | 2401.245

## 25-ReflectiveFilmWindows
Add Reflective Film Windows Payback
Building # | 1000 | Sample Building |  |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Note: Reducing solar glare can prolong life of furniture, carpet, and other surfaces from UV light. It also may increase productivity of workers if the glare makes it hard to see computer screens and compels them to open and close blinds to balance views, daylight, and excessive glare and heat gain on surfaces. Calculations do not factor these benefits from
Window film to be added to a total of 3 windows (4 West, 5 South) at second floor - each window approximately 3.5' x x 7'
Cooling load due to Solar Radiation: |  | q = sum (A x SC x MSHG x CLF) |  |  | 1 Btu = | 0.00029307 |  | kWh | Electric Rate ($ per KWh): |  | 0.09
|  |  | Existing | Proposed |  | Reduction of cooling load per hour (btu): |  |  |  | 5720 | Btu
A = window area (sq. feet) |  |  | 220 | 220 |  | Reduction of cooling load per day (12 hours): |  |  |  | 68640 | Btu
SC = shading coefficient |  |  | 1 | 0.48 |  | Reduction of cooling load per year (6 months): |  |  |  | 12355200 | Btu
MSHG = maximum solar heat gain (BTU/hr/sf) |  |  | 200 | 200 |  | Cooling COP |  |  |  | 2
CLF = cooling load factor |  |  | 0.25 | 0.25 |  | Reduction of kWh per year |  |  |  | 1810.4758 | kWh
q = cooling load (BTU/ hr) |  |  | 11000 | 5280 |  | Dollars saved per year |  |  |  | 162.9428
|  |  | Energy Savings | 1810.4758 | kWh |  |  |  | Implementation Cost | 3274.26
|  |  | Energy Cost Savings | 162.9428 |  |  |  |  | Simple Payback | 20.0945 | years
Description |  |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Install Window film designed to cut glare and heat gain using a proprietary crew. |  |  |  |  | SF | 220 | 4 | 3.5 | 0.1 | 7.6 | 1672
Lift rental and set up |  |  |  |  | EA | 1 | 0 | 0 | 800 | 800 | 800
Clean up |  |  |  |  | EA | 1 | 70 | 100 | 20 | 190 | 190
[6 empty] | Subtotal |  |  |  | 997.6 | 2662
[6 empty] | Contingency |  |  |  | 0.08 | 212.96
[6 empty] | OH |  |  |  | 0.05 | 133.1
[6 empty] | Profit |  |  |  | 0.1 | 266.2
[6 empty] | Total |  |  |  |  | 3274.26

## 26-WindowReplace
Window Replacement Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  | 2023-01-01
Example building has (24) 4'6" x 3'10" wood frame, single pane, pivoting clerestory windows. Assume an average of 1/32" gap on all sides of each window. Modify size of gaps for your building.
Heat Loss: | Q = V x Cp x DD x 24 hr/day x 60 min/hr |  |  |  |  | Infiltration: | V = I x A
Q = .018 x V x temp dif. | [5 empty] | V = ventilation air in CFM
Qyr = .018 x cubic ft. /day x degree days | [5 empty] | I = Excess Infiltration rate (cfm/sq ft)* = |  |  |  | 1.5
heat capacity of air (Btu/ CFt.)= |  |  | 0.018 |  |  | A = area of cracks/ openings in sq ft.
Convert: | 1 Btu = | 0.00029307 | kWh
cost per kWh: |  | 0.09 |  |  | Total length of gap (ft): |  |  |  | 16.666
cost per Mbtu: |  | 8 |  |  | Average gap width (in): |  |  |  | 0.03125
[5 empty] | area of each opening: |  |  |  | 0.043401 | sq feet
Heating COP: |  | 5 | (GSHP) |  | Total number of openings requiring attention: |  |  |  | 24
Cooling COP: |  | 5 | (GSHP) |  | V (CFM) = |  |  |  | 1.5624 | cfm
[5 empty] | Annual Heating degrees days: |  |  |  | 4865
Heating Energy Savings: |  | 197024.6187 | BTUs |  | Annual Cooling degree days: |  |  |  | 577
Cooling Energy Savings: |  | 23367.5653 | BTUs
*http://ibpsa-boston.com/minutes/IBPSAboston-presentations_2011-09-16_Gowri.pdf
http://www.cedengineering.com/upload/Heat%20Loss%20Calculations%20and%20Principles.pdf
Conductive Heat and Cooling Loss Calculation:
Heat loss: | Q = A x U x (Ti - To) | [6 empty] | Estimated Original U value: | 1.25
| Q = Total hourly rate of heat loss | [6 empty] | Estimated Proposed U value: | 0.6
| U = overall heat transfer coef. Btu/hr sq ft | [6 empty] | Net Area: | 414 | sq. ft.
A = Net area
| Ti = Inside design temp | [6 empty] | Heating Energy Savings: | 31420116 | BTUs
| To = Outside design temp | [6 empty] | Cooling Energy Savings: | 3726496.8 | BTUs
Total heat loss/ year = Area x U value x HDD x 24 hrs/day
Total Savings:
|  | Total Heating Energy Savings: | 31.6171 | MBTUs
|  |  | 1853.2138 | kWh |  |  |  | Total Energy Cost Savings: | 186.5708
|  | Total Cooling Energy Savings: | 3.7499 | MBTUs |  |  |  | Implementation Cost: | 1879.44
|  |  | 219.7954 | kWh |  |  |  | Simple Payback: | 10.0736 | Years
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Demo existing windows and frame |  |  |  | EA | 4 | 0 | 37 | 0 | 37 | 148
Picture window, insulated double pane, 4' x 4'6" w/ frame |  |  |  | EA | 1 | 1200 | 180 | 0 | 1380 | 1380
[5 empty] | Subtotal |  |  |  | 1417 | 1528
[5 empty] | Contingency |  |  |  | 0.08 | 122.24
[5 empty] | OH |  |  |  | 0.05 | 76.4
[5 empty] | Profit |  |  |  | 0.1 | 152.8
[5 empty] | Total |  |  |  |  | 1879.44
Note on K25: mbryan1: Single-pane, wood frame
Note on K26: mbryan1: Double-pane, Wood Frame
Note on K27: mbryan1: (24) windows at 4'6"x3'10"

## 27-WeatherStripDoors
Repair Weatherstripping at Outside Doors Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Air Infiltration Heat and Cooling Loss Calculations:
Assume that each door has a 1/8" x 7' opening at astragal where weatherstripping worn (0.125" x 84"/144 = .07 sq. ft)
Infiltration: | V = I x A |  |  |  | area of each opening |  |  |  | 0.07 | sq feet
V = ventilation air in CFM |  |  |  |  | Total number of openings requiring attention: |  |  |  |  | 4
I = Infiltration rate (cfm/sq ft)* = |  |  | 1.5 |  | V (CFM) = | 0.42
A = area of cracks/ openings in sq ft. |  |  |  |  | Annual Heating degrees days: |  |  |  | 4021
heat capacity of air (Btu/ CFt.)= |  |  | 0.018 |  | Annual Cooling degree days: |  |  |  | 580
Q = .018 x V x temp dif.
Qyr = .018 x cubic ft. /day x degree days
coversion of Btu/hr to KW: |  | 0.00029307 |  |  | KWh required for BTUs/ year |  |  |  | 5357.9954
cost per kW: |  | 0.09 |  |  | Cost of KW /yr required: |  |  |  | 482.2196
[5 empty] | Project cost from estimate worksheet |  |  |  | 878.343
BTU heating loss |  | 43774.2144 |  |  | Payback: |  |  |  | 1.8215 | Years
BTU cooling loss |  | 6314.112
Total BTUs (Q/day) |  | 50088.3264 | (Extra BTUs heating and cooling required per day)
BTUs per year: |  | 18282239.136
*http://ibpsa-boston.com/minutes/IBPSAboston-presentations_2011-09-16_Gowri.pdf
http://www.cedengineering.com/upload/Heat%20Loss%20Calculations%20and%20Principles.pdf
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Remove old weatherstripping, prep, repair tracks |  |  |  | ln. ft. | 28 | 0.05 | 4.5 | 0.75 | 5.3 | 148.4
Install new weatherstripping |  |  |  | ln. ft. | 28 | 4 | 15 | 1 | 20 | 560
Clean up |  |  |  | na | 6 | 0.4 | 0.5 | 0.05 | 0.95 | 5.7
[5 empty] | Subtotal |  |  |  | 26.25 | 714.1
[5 empty] | Contingency |  |  |  | 8% | 57.128
[5 empty] | OH |  |  |  | 5% | 35.705
[5 empty] | Profit |  |  |  | 10% | 71.41
[5 empty] | Total |  |  |  |  | 878.343

## 28-AutoDoorTime
Coordinate Open Time for Automatic Door Openers at Vestibule Payback
Building # | 1000 | Sample Building |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Doors have Automatic door operators used to provide access for disabled occupants. Assume both doors are open for 30 seconds each with combined opening into building of 20 seconds per cycle. Assume 20 cycles per hour. 8 hour day. Door size is approx. 4' x 7'. Worksheet estimates savings for coordinating time of openings to reduce time of opening.
Pressure at opening = 50 feet per minute (fpm) (experimentally derived)
Volume flow rate: 50fpm x door opening area x # of door openings x opening time in minutes/ working period
Sensible heat load Q (btu/hr) = 1.08 x cfm x (DB temp. of ambient air (btu/lb) - DB temp. of conditioned air)
Total load Q (btu/hr) = 4.5 x cfm x (entalpy of ambient air (btu/lb) - enthalpy of conditioned air (btu/lb))
Number of openings: | 1 | Area of door opening 4'x7' | 28 | Number of door openings per day |  | 160 | Duration of opening (mins.) |  | 0.33
Working period (minutes per day): |  | 480 | minute/ 24 hr day | 1440 | Volume flow rate /wkg per. (cfm): |  | 154 | Vol. flow rate / 24 hr | 51.3333
.018 = heat capacity of air Btu/ cubic foot |  |  |  |  | Annual Heating degrees days: |  |  | 3877
Q = .018 x V x temp dif. |  |  |  |  | Annual Cooling degree days: |  |  | 1564
Qyr = .018 x cubic ft. /day x degree days
conversion of Btu/hr to KW: |  | 0.00029307 |  | Extra BTUs heating and cooling required: |  |  |  | 120659.616
cost per kW: |  | 0.09 |  | KW required for BTUs/ year |  |  |  | 12907.0726
|  |  |  | Cost of KW /yr required: |  |  |  | 1161.6365
BTU heating loss: |  | 85976.352 |  | Project cost from estimate worksheet |  |  |  | 978.075
BTU cooling loss: |  | 34683.264 |  | Payback: |  |  |  | 0.84198
* http://www.cedengineering.com/upload/Heat%20Loss%20Calculations%20and%20Principles.pdf
http://ibpsa-boston.com/minutes/IBPSAboston-presentations_2011-09-16_Gowri.pdf
* http://www.eng-tips.com/viewthread.cfm?qid=75534
Description |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Add controls to reduce swing time to 15 - 20 seconds and interlock vestibule doors to prevent from staying open simultaneously |  |  | Ea. | 2 | 100 | 250 | 25 | 375 | 750
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Subtotal |  |  |  | 375 | 750
|  |  |  | Contingency |  |  |  | 8% | 60
|  |  |  | OH |  |  |  | 5% | 37.5
|  |  |  | Profit |  |  |  | 10% | 75
|  |  |  | Total |  |  |  |  | 922.5

## 29-AirCurtain
Add Air Curtain to Entrance Doors Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Air Infiltration Heat and Cooling Loss Calculations:
Calculations based on information provided by ASHRAE and air curtain manufacturer calculations including those by Powered Aire, Berger, and Leading Edge. Air curtains can be an acceptable substitute for vestibules in existing and some new construction applications.
Heating: |  |  | Cooling: |  |  |  | Operation:
Avg. Temp Outside (To) oF |  | 40 | Avg. Temp Outside (To) oF |  |  | 85 | Days per Week Building Open |  |  | 5
Avg. Temp Inside (Ti) oF |  | 68 | Avg. Temp Inside (Ti) oF |  |  | 68 | Hours per day Building in Use |  |  | 9
Average Heating Weeks |  | 32 | Average Cooling Weeks |  |  | 26 | Average Openings of Door per Hour |  |  | 200
Avg. wind speed (MPH) |  | 12 | Avg. Wind speed (MPH) |  |  | 8 | Average minutes per opening |  |  | 0.5
[7 empty] | Height (ft) | 7 | Width (ft) | 6
Door Coeficient (acounts for opening and angle): |  | 0.5 | Conversion factor for equation: feet per minute/miles per hour |  |  | 88 | Heating (no air curtain) |  | Cooling (no air curtain)
Air entering building due to wind in CFM: Qw = Ht. x Wd. X 88 x 0.5 x wind speed | [6 empty] | Qw: | 22176 | Qw: | 14784
Simplified ASHRAE formula for temp. diff. air infiltration: Qtd = H x W x ∆ T x 2 | [6 empty] | Qtd: | 2352 | Qtd: | 1428
Heat loss or gain through upening without Air Curtain (BTU/hour) : qD = 1.1 x QT x ∆ T | [6 empty] | QT: | 24528 | QT: | 16212
Simplified formula for Heat loss or gain with air curtain (BTU/hour): H x 220 x 1.1 x ∆ T | [6 empty] | BTU/hr (qD): | 755462.4 | BTU/hr (qD): | 303164.4
Heat Loss with Air Curtain (Heating ): |  |  | 47432 | Btu/hr | Heating Savings with Air Curtain (BTU/hr) |  | 708030.4 | Hours Doors open per year (Heating season) |  | 2400
Heat Loss with Air Curtain (Air cond. ): |  |  | 28798 | Btu/hr | Cooling Savings with Air Curtain (BTU/hr) |  | 274366.4 | Hours Doors open per year (Cooling season) |  | 1950
Energy Unit Conversion Table |  |  |  |  | Heating + Cooling Energy use WITHOUT Air Curtain ( BTUs) |  |  |  |  | 2404280340
Input | unit | conversion | Output | unit | Heating + Cooling Energy use WITH Air Curtain ( BTUs) |  |  |  |  | 169992900
1 | BTU | 0.00029307 | 0.00029307 | kWh | Heating + Cooling Energy Savings WITH Air Curtain (BTUs) |  |  |  |  | 2234287440
1 | kWh | 3412.1416 | 3412.1416 | BTU
1000 | BTU | 0.001 | 1 | mBtu |  | Air Curtain operation = Kw x hours (based on HP)
1 | Horsepower | 0.7457 |  | kW |  | HP: | 0.5 | KWh used per year |  | 1621.8953
| cost per kW: | 0.09
| Total Energy Saved |  |  | 653183.1154 | KWh | Cost from estimate worksheet |  |  | 19034.8035
| Total Cost of energy saved per year: |  |  | 58786.4804 |  | Payback (years) |  |  | 0.3238
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Prepare opening for Air Curtain including wiring |  |  |  | EA | 1 | 120 | 250 | 15 | 385 | 385
Install new Air Curtain and adjust |  |  |  | EA | 1 | 12500 | 2400 | 150 | 15050 | 15050
Clean up |  |  |  | na | 1 | 0.4 | 40 | 0.05 | 40.45 | 40.45
[5 empty] | Subtotal |  |  |  | 15475.45 | 15475.45
[5 empty] | Contingency |  |  |  | 8% | 1238.036
[5 empty] | OH |  |  |  | 5% | 773.7725
[5 empty] | Profit |  |  |  | 10% | 1547.545
[5 empty] | Total |  |  |  |  | 19034.8035

## 30-RevolvingDoors
Replace Vestibule Doors with Revolving Door Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 0
Air Infiltration Heat and Cooling Loss Calculations:
Calculations done based on PNL study and MIT study showing that revolving doors save 8 times airflow of conventional doors, especially in buildings with large occupant traffic that results in large amount of time with doors open to exterior.
Heating: |  |  | Cooling: |  |  |  | Operation:
Avg. Temp Outside (To) oF |  | 40 | Avg. Temp Outside (To) oF |  |  | 85 | Days per Week Building Open |  |  | 5
Avg. Temp Inside (Ti) oF |  | 68 | Avg. Temp Inside (Ti) oF |  |  | 68 | Hours per day Building in Use |  |  | 9
Average Heating Weeks |  | 32 | Average Cooling Weeks |  |  | 26 | Average Openings of Door per Hour |  |  | 200
Avg. wind speed (MPH) |  | 12 | Avg. Wind speed (MPH) |  |  | 8 | Height (ft) | 7 | Width (ft) | 6
Air entering building in CFM: (ASHRAE Handbook) Q = CA *A * Rp |  |  |  |  | BTU's per Hour needed heat or cool infiltrating/ exfiltrating air = ∆T x 1.08 x Q
Q = air flow in CFM
CA is Air Flow Coefficient from chart below (cfm/ft2 - (in. of water)0.5) |  |  |  |  | 500 |  | Heating (existing) |  | Cooling (existing)
A is area of the door opening (ft2) |  |  |  |  | 84 |  | Q = | 16800 | Q = | 16800
Rp is pressure factor in inches of water (avg. from chart below) |  |  |  |  | 0.4 |  | BTU/hr | 470400 | BTU/hr | 285600
(note - Air Flow Coeficient assumed no vestibule because ADAG openers stay opened together) | [6 empty] | hours/year | 1440 | hours/ year | 1170
Number of doors |  |  |  |  | 2 |  | BTU/year | 677376000 | BTU/year | 334152000
Energy Unit Conversion Table | [6 empty] | Heating (w/ rev. door) |  | Cooling (w/ rev. door)
Input | unit | conversion | Output | unit |  |  |  | 84672000 |  | 41769000
1 | BTU | 0.00029307 | 0.00029307 | kWh
1 | kWh | 3412.1416 | 3412.1416 | BTU |  |  | Savings (BTU): | 592704000 | Savings(BTU): | 292383000
1000 | BTU | 0.001 | 1 | mBtu
1 | Horsepower | 0.7457 |  | kW |  |  | Savings (kWh): | 173704.3955 | Savings (kWh): | 85688.9987
| cost per kW: | 0.09 |  |  |  |  | Savings $): | 15633.3956 | Savings ($): | 7712.0099
| Total Energy Saved |  |  | 259393.3941 | KWh | Cost from estimate worksheet |  |  | 337813.9035
| Total Cost of energy saved per year: |  |  | 23345.4055 |  | Payback (years) |  |  | 14.4703
http://www.pnl.gov/main/publications/external/technical_reports/PNNL-20026.pdf
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Remove existing vestibule doors, patch drywall |  |  |  | EA | 4 | 300 | 1200 | 40 | 1540 | 6160
Prepare foundation for new door and other site work to prepare for new doorway construction |  |  |  | EA | 1 | 3500 | 5300 | 400 | 9200 | 9200
Construct new walls and roof for entrance area, install new ATFP flanking egress doors. |  |  |  | EA | 1 | 48000 | 28000 | 1000 | 77000 | 77000
Install new 12' revolving door and adjust with factory trained technicians, verify operation |  |  |  | EA | 1 | 105000 | 18000 | 125 | 123125 | 123125
Exterior finish work for door |  |  |  | EA | 1 | 2240 | 7500 | 20 | 9760 | 9760
Install sliding ATFP doors |  |  |  | EA | 2 | 3500 | 5000 | 100 | 8600 | 17200
Site work -new walk to door and low retaining wall |  |  |  | EA | 1 | 8500 | 23000 | 300 | 31800 | 31800
Clean up |  |  |  | na | 1 | 0.4 | 400 | 0.05 | 400.45 | 400.45
[5 empty] | Subtotal |  |  |  | 261425.45 | 274645.45
[5 empty] | Contingency |  |  |  | 0.08 | 21971.636
[5 empty] | OH |  |  |  | 0.05 | 13732.2725
[5 empty] | Profit |  |  |  | 0.1 | 27464.545
[5 empty] | Total |  |  |  |  | 337813.9035

## 31-TreeShade
Plant Trees to Reduce Glare and Provide Shade Payback
Building # | 1000 | Sample Building |  |  |  | Navy Base |  |  |  |  | Washington DC |  |  | 0
Cooling Load Reduction on Building Envelope Due to Shading by Trees in Cooling Season
Calculations based on trees that have been watered during drought periods and achieve 10 years of healthy growth in place. Benefits of shading increase in future years as trees mature and grow larger.
Q = A x U x (Ti - To) | [5 empty] | cost per kW: | [6 empty] | 0.09
Q = Total hourly rate of heat loss | [5 empty] | Shaded surface width (ft): | [6 empty] | 150
U = overall heat transfer coef. Btu/hr sq ft | [5 empty] | Shaded surface height (ft): | [6 empty] | 30
A = Net area | [5 empty] | Estimated Average U value: | [6 empty] | 0.25
Ti = Inside design temp | [5 empty] | Surface Area: | [6 empty] | 4500 | sq. ft.
To = Outside design temp | [5 empty] | Total heat loss/ year = Area x U value x CDD x 12 hrs/day
[6 empty] | Total yearly cooling Loss @ 72 deg. F: | [6 empty] | 47620650 | BTUs
Cooling Degrees Days without tree shade: |  |  |  | 775 |  | Total yearly cooling Loss @ 78 deg. F: | [6 empty] | 19355490 | BTUs
Cooling Degrees Days with tree shade |  |  |  | 315 | [7 empty] | Savings: | 28265160 | BTUs
Convert BTUs to KWh: 1 BTU/hr = 0.00029307107 kW
(source: www.degreedays.net (using temperature data from www.wunderground.com) Assume 20 deg. ∆T cooler for shaded areas (http://www.epa.gov/heatisland/mitigation/trees.htm ) | [11 empty] | Savings: | 8283.7007 | KWh
[12 empty] | Cost Savings: | 745.5331
[11 empty] | Simple Payback (years) |  | 5.1343
Cooling Benefits from shading of existing windows - Solar Gain Reduction
Calculations assume that trees are providing shading from intense morning sun which reduces heat gain through windows.
Cooling load due to Solar Radiation: |  |  |  |  | Exist. | Proposed |  |  | Reduction of Cooling load/ hour (btu): |  |  |  |  | 26000
q = sum (A x SC x MSHG x CLF) |  |  |  |  | 50000 | 24000 |  |  | Reduction of cooling load/ day (6 hours): |  |  |  |  | 156000
q = cooling load (BTU/ hr) | [8 empty] | Reduction of cooling load /year (6 months): |  |  |  |  | 28080000
A = window area (sq. feet) |  |  |  |  | 1000 | 1000 | [5 empty] | 1 BTU = .00029307107017 kWh
SC = shading coefficient |  |  |  |  | 1 | 0.48 | [5 empty] | Reduction of kWh per year |  | 8229.4357
MSHG = maximum solar heat gain (BTU/hr/sq. ft) |  |  |  |  | 200 | 200 | [5 empty] | Dollars saved per year |  | 740.6492
CLF = cooling load factor |  |  |  |  | 0.25 | 0.25 | [5 empty] | Simple Payback (years) |  | 5.1681
Benefits from daylighting with exterior glare controlled - Reduction of Artificial Lighting
Calculations assume that with proper shading the intense morning glare is reduced and the windows can be left open without full shading. This accounts also for the fact that once the shades are closed in the morning they often are not re-opened unless the buildng staff is trained.
| Device Properties | [5 empty] | Quantity and Use |  |  |  | Energy Savings |  |  | Replacement
| Type | Watts | Initial Lumens | Efficiency Loss | Service Life (hours) | Device Cost | Quantity | hours/ day | days/ week | weeks | KW hours | KWh saved | Annual KWh Cost Savings | Annual Replacement Cost
Existing | T-8 | 45 | 2500 | 75% | 15000 | 3 | 30 | 6 | 7 | 52 | 2948.4 | 1965.6 | 176.904 | 13.104
Proposed | T-8 | 45 | 2500 | 75% | 15000 | 3 | 30 | 2 | 7 | 52 | 982.8 |  |  | 4.368
Replacement Cost Savings: |  | Replacement $ = Quantity of devices x cost per item x hours / service life | [5 empty] | Total Annual Savings |  | 185.64 |  | Annual KWh Saved | Annual KWh Cost | An. Rep. Cost sav.
|  | Simple Payback (years) |  |  |  | 20.6193 | [5 empty] | 1965.6 | 176.904 | 8.736
Total Benefits
Total Energy Savings (KWh) |  |  |  | 18478.7363 |  |  |  | Total Implementation Cost |  |  |  |  | 3827.76
Total Energy Savings ($) |  |  |  | 1663.0863 |  |  |  | Payback (years) |  |  |  |  | 2.3016
Implementation Cost
Description |  |  |  |  | unit | QTY | material per unit |  | labor per unit |  | Equipment Per Unit |  | total per unit | Total
Survey for buried utilities (office and field work) as required. Measure and mark location for trees. |  |  |  |  | linear feet | 150 | 0 |  | 2.25 |  | 0.05 |  | 2.3 | 345
Prepare tree wells for trees. Add organic fertilizer to amend soil at a rate of 2 bags per tree pit. |  |  |  |  | ea | 6 | 20 |  | 50 |  | 2 |  | 72 | 432
Install 2" caliper white oak (Quercus alba), backfill, water, provide guy wires with hose padding, add 2" mulch at base |  |  |  |  | ea | 6 | 200 |  | 150 |  | 30 |  | 380 | 2280
Clean up |  |  |  |  | ls | 1 | 5 |  | 30 |  | 20 |  | 55 | 55
[9 empty] | Subtotal |  |  |  | 509.3 | 3112
Note: Estimate based on Material price through government procurement rather than full retail nursery price. If a non-profit organization such as Casey Trees is involved (as they currently are on base) the price could be significantly lower for this project. | [8 empty] | Contingency |  |  |  | 8% | 248.96
[9 empty] | OH |  |  |  | 5% | 155.6
[9 empty] | Profit |  |  |  | 10% | 311.2
[9 empty] | Total |  |  |  |  | 3827.76

## 32-LightSensors
Add Daylighting Sensors Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  |  |  | Washington DC |  |  |  | 2023-01-01
Install daylighting sensors in applicable spaces | [10 empty] | Electric Rate ($ per KWh): |  |  |  | 0.09
KWh = Watts x hours/ 1000
Annual savings = Rate x KWh
Location |  | Device Properties |  |  |  |  | Quantity and Use |  |  |  |  | Energy Savings |  |  | Replace
|  | Type | Watts | Initial Lumens | Service Life (hours) | Device Cost | Approximate Quantity | hours/ day | days/ week | weeks | Estimated Daylighting savings | kWh | KWh saved | Annual KWh Cost Savings | Annual Replacement Cost
Office 233 | Existing | 4ft 3-lamp 32W T8 | 96 | 2850 | 30000 | 4 | 6 | 12 | 5 | 52 |  | 1797.12 | 539.136 | 48.5222 | 2.496
[12 empty] | 0 |  |  | 0
| Proposed | 4ft 3-lamp 32W T8 | 96 | 2850 | 30000 | 4 | 6 | 12 | 5 | 52 | 30% | 1257.984 |  |  | 1.7472
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30% | 0 |  |  | 0
[8 empty] | Total Savings |  |  |  |  | An.KWh Saved | Annual KWh Cost | An. Rep. Cost sav.
Daylight Sensors Required to control subject lamps: |  |  |  |  | 1 | [7 empty] | 539.136 | 48.5222 | 0.7488
Replacement Cost Savings: |  |  | Replacement $ = Quantity of devices x cost per item x hours / service life
|  |  |  | Total Energy Savings (KWh) | 539.136 | [7 empty] | Total Implementation Cost | 431.73
|  |  |  | Total energy Cost Savings ($) | 49.271 | [7 empty] | Simple Payback (years) | 8.7623
Description |  |  |  |  | unit | QTY |  | material per unit |  | labor per unit |  | Equipment Per Unit | total per unit | Total
Install Daylight Sensor |  |  |  |  | SF | 1 |  | 220 |  | 130 |  | 1 | 351 | 351
[10 empty] | Subtotal |  |  | 351 | 351
| Assume 30% typical lighting energy savings | [8 empty] | Contingency |  |  | 0.08 | 28.08
| Reference: | [8 empty] | OH |  |  | 0.05 | 17.55
| http://aceee.org/files/proceedings/2006/data/papers/SS06_Panel3_Paper19.pdf | [8 empty] | Profit |  |  | 0.1 | 35.1
[10 empty] | Total |  |  |  | 431.73

## 33-OccSensors
Install Occupancy Sensors Payback
Building # | 1000 | Sample Building |  |  |  | Navy Base |  |  |  |  | Washington DC |  |  |  | 2023-01-01
Occupancy Sensors save energy by turning off luminairs when space is not occupied, both saving electricity and cooling load for HVAC system. | [11 empty] | Electric Rate ($ per KWh): |  |  | 0.09
KWh = Watts x hours/ 1000
Annual savings = Rate x KWh
Location |  | Device Properties | [5 empty] | Quantity and Use |  |  |  | Energy Savings |  |  | Replace
|  | Type | Watts | Initial Lumens | Efficiency Loss | Service Life (hours) | Device Cost | Quantity | hours/ day | days/ week | weeks | KW hours | KWh saved | Annual KWh Cost Savings | Annual Replacement Cost
First Floor | Existing | 2'X4' 32W T8 3 lamps | 96 | 2800 | 75% | 20000 | 4.5 | 504 | 6 | 7 | 52 | 105670.656 | 70447.104 | 9510.359 | 247.6656
| Proposed | 2'X4' 32W T8 3 lamps | 96 | 2800 | 79% | 20000 | 4.5 | 504 | 2 | 7 | 52 | 35223.552 |  |  | 82.5552
[13 empty] | 0 | 0
Although HID lamps are very efficient in theory there are efficiency losses due to use and on-off cycling degregation, 360 degrees light loss to reflector, lens degregation and dirt, and other factors. Source effiency 120 lumens/ watt - actual efficiency 30 lumens/watt. LED source 100 lumens/ watt - actual 50 lumens/ watt http://www.innovativelight.com/hid-vs-led-lighting/ | [8 empty] | Total Savings |  |  |  | Annual KWh Saved | Annual KWh Saving | An. Rep. Cost
[13 empty] | 70447.104 | 9510.359 | 82.5552
Replacement Cost Savings: |  |  | Replacement $ = Quantity of devices x cost per item x hours / service life
Total Energy Savings (KWh) |  |  |  | 70447.104 |  |  |  | Total Implementation Cost | [5 empty] | 15394.31
Total Energy Savings ($) |  |  |  | 9592.9142 |  |  |  | Payback (years) | [5 empty] | 1.6047
Implementation Cost
Description of work | [5 empty] | Total items | Labor Cost per hour |  | Labor hours/ item |  | Material cost/item | Equip. Cost /item | Total Cost
Install wall mounted occupancy sensor main building floor | [5 empty] | 28 | 90 |  | 3.5 |  | 135 | 5 | 12740
Contigency | [5 empty] | 1 | 70 |  | 6 |  | 50 | 4 | 474
[10 empty] | SUBTOTAL |  |  | 13214
[10 empty] | OVERHEAD (15%) |  |  | 1982.1
[10 empty] | PROFIT (10%) |  |  | 198.21
[10 empty] | TOTAL COST |  |  | 15394.31
Note on B22: Boyd, Andrew F CIV NAVFAC Washington:
Note on B24: Boyd, Andrew F CIV NAVFAC Washington:

## 34-LampWattage
Reduce Lamp Wattage Payback
Building # | 1000 | Sample Building |  |  |  | Navy Base |  |  |  |  | Washington DC |  |  | 2023-01-01
Spreadsheet provides two calculation strategies for reducing wattage of existing flourescent fixtures. One involves reducing number of lamps where the lighting levels are higher than needed. The other uses marginal cost of relamping to install lower wattage bulbs. Note orginal spreadsheet by CH2Mhill was done in 2015 and LED lighting has become much more economical - spreadsheet canbe modified for LED bulbs. | [10 empty] | Electric Rate ($ per KWh): |  |  | 0.09
KWh = Watts x hours/ 1000
Annual savings = Rate x KWh
Some interior lighting in the kitchen and some office spaces is provided by 4-lamp fixtures and are generally overlit (~65 fc). Delamp to 2 lamps/fixture. E
Location |  | Device Properties |  |  |  |  | Quantity and Use |  |  |  | Energy Savings |  |  | Replace
|  | Type | Watts Per Lamp | Average Footcandles | Existing Lamp Count | Proposed Lamp Count | Approximate Fixture Quantity | hours/ day | days/ week | weeks | KWh saved | KWh saved | Annual KWh Cost Savings | Initial Cost
Various offices and corridors. Approx 1/2 of spaces were unoccupied. |  | 4L T-8 | 32 | ~65 | 4 | 2 | 70 | 8 | 5 | 52 | 9318.4 | 9318.4 | 838.656 | 525
|  | Total Energy Savings (KWh) |  |  | 9318.4 |  |  |  | Total Implementation Cost |  |  | 525
|  | Total Energy Cost Savings ($) |  |  | 838.656 |  |  |  | Simple Payback (years) |  |  | 0.626
Existing lamps are 32 W. As part of future lamp replacement or group relamp activities, install 25 W lamps as standard replacements for 32 W T8 4' lamps. Note: the cost estimating is based on the difference in cost between replacing with 32 W lamp, not the total cost of labor plus material for 25 W lamp. Calculation is configured as a procurement policy
Location | Device Properties | [5 empty] | Quantity and Use |  |  | Energy Savings |  |  |  | Replace
| Existing Type | Existing Watts Per Lamp | Proposed Type | Proposed Watts Per Lamp | Average Footcandles | Approximate Lamp Quantity | hours/ day | days/ week | weeks | KWh saved | Power Saved (kW) | Energy Saved (kWh) | Annual KWh Cost Savings | Initial Cost
Throughout | 32W 4ft T8 | 32 | 25W 4ft T8 | 25 | 40-60 | 450 | 12 | 5 | 52 | 9828 | 4.14 | 12916.8 | 1162.512 | 2250
Entry | 60W Incand. | 60 | 10.5W LED | 10.5 | 35-45 | 20 | 12 | 5 | 52 | 3088.8 |  |  |  | 50
| Total Energy Savings |  | 12916.8 | kWh | [5 empty] | Total Implementation Cost |  | 5645
| Total Energy Cost Savings |  | 1162.512 | [6 empty] | Simple Payback |  | 4.8559 | years
Implementation Cost
Division # | Description of work | [6 empty] | Total items | Labor Cost per hour | Labor hours/ item | Material cost/item | Equip. Cost /item | Total Cost
26 05 05.50 | Remove existing flourescent lamps from existing fixture to delamp | [6 empty] | 70 | 75 | 0.1 | 0 | 0 | 525
260505.50 | Remove existing flourescent lamps from existing fixture to replace | [6 empty] | 450 | 75 | 0 | 5 | 0 | 2250
266123.10 | Marginal cost of relamping existing T8 32W to lower Wattage T8 25W | [6 empty] | 450 | 75 | 0.1 | 4 | 0 | 5175
260505.50 | Remove existing incandescent lamps from existing fixture to replace | [6 empty] | 20 | 75 | 0 | 2.5 | 0 | 50
266123.55 | Marginal cost of relamping existing 60W incandescent to 10.5 W LED | [6 empty] | 20 | 75 | 0.1 | 16 | 0 | 470
[10 empty] | SUBTOTAL |  |  | 8470
[10 empty] | OVERHEAD (5%) |  |  | 423.5
[10 empty] | PROFIT (10%) |  |  | 42.35
[10 empty] | TOTAL COST |  |  | 8935.85
Note on C29: Boyd, Andrew F CIV NAVFAC Washington:
Note on C30: Boyd, Andrew F CIV NAVFAC Washington:
Note on C31: Boyd, Andrew F CIV NAVFAC Washington:
Note on C32: Boyd, Andrew F CIV NAVFAC Washington:
Note on C33: Boyd, Andrew F CIV NAVFAC Washington:

## 35-OutsideLED
Replace Outdoor Lights With LED Payback
Building # | 1000 | Sample Building |  |  |  | Navy Base |  |  |  |  | Washington DC |  |  | 2023-01-01
Replace 20 Exterior HID floodlights with LED dark sky compliant fixtures, Re-lamp 0 existing HID decorative fixtures with LED lamps, and repair 1 broken photocell (*existing photocell) | [11 empty] | Electric Rate ($ per KWh): |  |  | 0.09
KWh = Watts x hours/ 1000
Annual savings = Rate x KWh
Location |  | Device Properties | [5 empty] | Quantity and Use |  |  |  | Energy Savings |  |  | Replace
|  | Type | Watts | Initial Lumens | Efficiency Loss | Service Life (hours) | Device Cost | Quantity | hours/ day | days/ week | weeks | KW hours | KWh saved | Annual KWh Cost Savings | Annual Replacement Cost
Building Exterior -flood | Existing | HID | 300 | 24000 | 75% | 10000 | 40 | 18 | 12 | 7 | 52 | 23587.2 | 22713.6 | 2044.224 | 314.496
| *Existing photocell | HID | 300 | 24000 | 75% | 10000 | 40 | 2 | 24 | 7 | 52 | 5241.6 |  |  | 69.888
| Proposed | LED | 200 | 18000 | 20% | 60000 | 250 | 7 | 12 | 7 | 52 | 6115.2 |  |  | 127.4
Building Exterior - decorative entrance | Existing | HID | 300 | 24000 | 75% | 10000 | 40 | 0 | 12 | 7 | 52 | 0 | 0 | 0 | 0
| Proposed | LED | 200 | 18000 | 20% | 60000 | 80 | 0 | 12 | 7 | 52 | 0 |  |  | 0
Although HID lamps are very efficient in theory there are efficiency losses due to use and on-off cycling degregation, 360 degrees light loss to reflector, lens degregation and dirt, and other factors. Source effiency 120 lumens/ watt - actual efficiency 30 lumens/watt. LED source 100 lumens/ watt - actual 50 lumens/ watt http://www.innovativelight.com/hid-vs-led-lighting/ | [8 empty] | Total Savings |  |  |  | Annual KWh Saved | Annual KWh Cost | An. Rep. Cost sav.
[13 empty] | 22713.6 | 2044.224 | 256.984
Replacement Cost Savings: |  |  | Replacement $ = Quantity of devices x cost per item x hours / service life
Implementation Cost
Description of work | [5 empty] | Total items | Labor Cost per hour |  | Labor hours/ item |  | Material cost/item | Equip. Cost /item | Total Cost
Remove existing floodlight fixtures | [5 empty] | 20 | 60 |  | 0.5 |  | 0 | 1 | 620
Install new wall mounted floodlights | [5 empty] | 20 | 70 |  | 1 |  | 400 | 4 | 9480
Relamp existing decorative entrance fixtures | [5 empty] | 0 | 75 |  | 0.5 |  | 80 | 4 | 0
[10 empty] | SUBTOTAL |  |  | 10100
[10 empty] | OVERHEAD (5%) |  |  | 505
[10 empty] | PROFIT (10%) |  |  | 50.5
[10 empty] | TOTAL COST |  |  | 10655.5
Total Energy Savings (KWh) |  |  |  | 22713.6 |  |  |  | Total Implementation Cost | [5 empty] | 10655.5
Total Energy Savings ($) |  |  |  | 2301.208 |  |  |  | Payback (years) | [5 empty] | 4.1652
Note on B20: Boyd, Andrew F CIV NAVFAC Washington:
Note on B21: Boyd, Andrew F CIV NAVFAC Washington:
Note on B22: Boyd, Andrew F CIV NAVFAC Washington:

## 36-InsideLED
Replace Indoor Lights With LED Payback
Building # |  | 1000 |  |  | Sample Building | [6 empty] | Navy Base | [5 empty] | Washington DC |  |  |  | 2023-01-01
Spreadsheet was developed for large project at USNA to show savings involving converting all existing fixtures to LEDs. Project also accounted for dimming capability and better occupancy controls for typical classroooms and other spaces. Original project involved over 30 different light fixure types and over 3000 fixtures.
[19 empty] | Electric Rate ($ per KWh): |  |  | 0.09
Location |  | Device Properties | [9 empty] | Quantity and Use |  |  |  |  | BTU savings |  | Energy Savings |  |  | Maintenance Savings
|  | Type | Lamp rated watts | Lamps per fixture | Watts | Average lumens per watt | Efficiency Loss (ballast + reflective) | Estimated Lumens | Service Life (hours) | Dimming Reduction | Device Cost with labor | Quantity | hours/ day | upgrade motion sensor reduction | days/ week | weeks | KILO BTU's (3.4/hr/watt) | KILO BTU's Saved | KW hours | KWh saved | Annual KWh Cost Savings | Annual Replacement Cost | Annual Replacement Cost Savings
Type A | Existing | T-5 | 32 | 3 | 96 | 60 | 75% | 4320 | 10000 | 0% | 24 | 38 | 8 | 2 | 5 | 52 | 25798.656 | 15721.056 | 7587.84 | 4623.84 | 416.1456 | 189.696 | 123.3024
| Proposed | LED | 50 | 1 | 50 | 85 | 95% | 4037.5 | 50000 | 50% | 56 | 38 | 6 |  | 5 | 52 | 10077.6 |  | 2964 |  |  | 66.3936
Type B | Existing | T-8 | 32 | 2 | 64 | 60 | 75% | 2880 | 10000 | 0% | 24 | 0 | 10 | 4 | 5 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Proposed | LED | 18 | 1 | 18 | 85 | 95% | 1453.5 | 50000 | 50% | 56 | 0 | 6 |  | 5 | 52 | 0 |  | 0 |  |  | 0
Type C | Existing | HALO. | 32 | 1 | 32 | 60 | 75% | 1440 | 10000 | 0% | 18 | 50 | 8 | 5 | 5 | 52 | 11315.2 | 9458.8 | 3328 | 2782 | 250.38 | 187.2 | 167.7
| Proposed | LED | 14 | 1 | 14 | 85 | 95% | 1130.5 | 50000 | 50% | 25 | 50 | 3 |  | 5 | 52 | 1856.4 |  | 546 |  |  | 19.5
Type D | Existing | CFL | 23 | 1 | 23 | 60 | 75% | 1035 | 10000 | 0% | 18 | 0 | 8 | 2 | 5 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Proposed | LED | 14 | 1 | 14 | 85 | 95% | 1130.5 | 50000 | 50% | 25 | 0 | 6 |  | 5 | 52 | 0 |  | 0 |  |  | 0
Type E | Existing | HID | 50 | 1 | 50 | 60 | 75% | 2250 | 10000 | 0% | 18 | 0 | 10 | 4 | 5 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Proposed | LED | 24 | 1 | 24 | 85 | 95% | 1938 | 50000 | 50% | 25 | 0 | 6 |  | 5 | 52 | 0 |  | 0 |  |  | 0
|  | Estimated Total Annual Cost Savings per Year |  |  |  |  | Estimated KWh Savings per year |  |  | Cost of KW saved per year used for Cooling |  |  |  | KW cooling required at 0.7 Kw per Ton |  |  | Est.Tons of Cooling saved | Annual Total Kilo BTU's saved |  | Annual KWh Saved | Annual KWh Cost Savings |  | Annual Maint. Cost Savings
|  | 1056.6737 |  |  |  |  | 8507.4587 |  |  | 99.1457 |  |  |  | 1101.6187 |  |  | 1573.741 | 25179.856 |  | 7405.84 | 666.5256 |  | 291.0024

## 37-Plumbing
Upgrade Plumbing Fixtures Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Spreadsheet can be modified to calculate savings for fixing fixture water leaks by substituting either measured drip rate using a drip guage such as the fishnick model ( http://fishnick.com/leakcalculator/ ) or estimate (average 4 gallons per day). Modify the existing and proposed consumption cells manually and use the plumber crew estimate row and insert cost figures in spreadsheet.
Results |  |  |  | Basic Inputs
Water Cost Savings |  | 2169.4281 |  | # Male FTE |  | 80 |  | Water Cost | 4.18 | $/kgal
Thermal Cost Savings |  | 495.9571 |  | # Female FTE |  | 80 |  | Sewer Cost | 4.86 | $/kgal
Total Cost Savings |  | 2665.3852 |  | DHW DeltaT |  | 80 | °F | Elec Cost | 26.697 | $/Mbtu
|  |  |  | Fuel Source |  | Fuel Oil |  | Steam Cost | 33.64 | $/Mbtu
Cost Estimate to Upgrade Selected Fixtures: |  | 40930.71 |  | Water Heater Efficiency |  | 85% |  | Gas Cost | 8 | $/Mbtu
Simple Payback: |  | 15.3564 | Years | Days Occupied per week |  | 5 | days/week | Fuel Oil Cost | 22.42 | $/Mbtu
|  |  |  | Specific heat of water |  | 8.33 | btu/gal-°F | Propane Cost | 14.35 | $/Mbtu
Fixture Constants |  | Water Closet | Urinal | Lavatory | Sink | Janitor | Shower | Dishwasher | Laundry Washer
Existing Consumption (gpf or gpm) |  | 3.5 | 1.5 | 2.2 | 2.5 | 5 | 2.5 | 6 | 31
Proposed Consumption (gpf or gpm) |  | 1.28 | 0.125 | 0.5 | 1 | 5 | 1.5 | 4 | 14
Duration of Use (mins) |  | 1 | 1 | 0.2 | 5 | 2 | 1.875 | 1 | 1
Uses per Day |  | 320 | 160 | 480 | 1 | 1 | 1 | 2 | 2
% Hot Water |  | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 0.25
Water Use Reduction
Enter Number of Fixtures in Facility |  | 12 | 6 | 11 | 2 | 0 | 17 | 0 | 0
Enter Number of Fixtures to Change (for Cost Estimate) |  | 12 | 0 | 11 | 2 | 0 | 17 | 0 | 0
Existing Water Usage Daily (gal) |  | 1120 | 0 | 211.2 | 25 | 0 | 79.6875 | 0 | 0
Proposed Water Usage Daily (gal) |  | 409.6 | 0 | 48 | 10 | 0 | 47.8125 | 0 | 0
Water Savings Daily (gal) |  | 710.4 | 0 | 163.2 | 15 | 0 | 31.875 | 0 | 0
FacilityTotal Water Reduction |  | 920.475 | gals daily | 239980.9821 | gals annually
Water Cost Reduction
Cost Savings Water Daily |  | 2.9695 | 0 | 0.68218 | 0.0627 | 0 | 0.13324 | 0 | 0
Cost Savings Sewer Daily |  | 3.4525 | 0 | 0.79315 | 0.0729 | 0 | 0.15491 | 0 | 0
Total Cost Savings Daily |  | 6.422 | 0 | 1.4753 | 0.1356 | 0 | 0.28815 | 0 | 0
Facility Water Cost Savings |  | 8.3211 | daily | 2169.4281 | annually
HW Heating Reduction
Hot Water Savings Daily (gal) |  | 0 | 0 | 81.6 | 7.5 | 0 | 19.125 | 0 | 0
Facility Hot Water Savings |  | 108.225 | gal daily | 28215.8036 | gals annually
HW Energy Savings Daily (Btu) |  | 0 | 0 | 54378.24 | 4998 | 0 | 12744.9 | 0 | 0
Cost Savings at Water Heater
Cost Electric Savings Daily |  | NA | NA | NA | NA | NA | NA | NA | NA
Cost Steam Savings Daily |  | NA | NA | NA | NA | NA | NA | NA | NA |  | Fuel | Efficiency
Cost Gas Savings Daily |  | NA | NA | NA | NA | NA | NA | NA | NA |  | Electric | 100%
Cost Fuel Oil Savings Daily |  | 0 | 0 | 1.4343 | 0.13183 | 0 | 0.33617 | 0 | 0 |  | Steam | 74.07%
Cost Propane Savings Daily |  | NA | NA | NA | NA | NA | NA | NA | NA |  | Gas | 86.96%
Facility Thermal Cost Savings |  | 1.9023 | daily | 495.9571 | annually | [5 empty] | Fuel Oil | 76.92%
[11 empty] | Propane | 86.96%
Summary
Individual Fixture Total Annual Cost Savings |  | 1674.3113 | 0 | 758.5832 | 69.7227 | 0 | 162.768 | 0 | 0
Individual Fixture Upgrade Cost |  | 23460 | 0 | 7755 | 90 | 0 | 1972 | 0 | 0
Individual Fixture Simple Payback (years) |  | 14.0117 | 0 | 10.223 | 1.2908 | 0 | 12.1154 | 0 | 0
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
22 42 13.40 | Demo ex. WC, install new 1.28 gpf WC, flush valve, repair finishes, clean up. |  |  | each | 12 | 1200 | 750 | 5 | 1955 | 23460
22 42 13.30 | Demo ex.urinal, install new ULF urinal, repair finishes, clean up. |  |  | each | 0 | 1800 | 750 | 5 | 2555 | 0
| Install lavatory aerator to reduce flow rate on sink |  |  | each | 2 | 20 | 25 | 0 | 45 | 90
| Install lavatory aerator to reduce flow rate on janitor sink |  |  | each | 0 | 20 | 25 | 0 | 45 | 0
22 42 39.10 | Remove ex.faucet, install new IR faucet, repair finishes, clean up. |  |  | each | 11 | 500 | 200 | 5 | 705 | 7755
22 42 23.40 | Remove ex.shower head, install 1.6 gmp head, repair finishes, clean up. |  |  | each | 17 | 80 | 35 | 1 | 116 | 1972
3100/3110 | Remove ex.dishwasher, install Energy Star DW, clean up. |  |  | each | 0 | 1200 | 450 | 10 | 1660 | 0
22 42 23.40 | Remove ex.Washing machine, install Energy Star model, clean up. |  |  | each | 0 | 1200 | 400 | 10 | 1610 | 0
Crew Q-1 | Plumber crew to repair leaky fixtures - avg 4 gal/day - parts and labor |  |  | each | 0 | 120 | 200 | 5 | 325 | 0
[5 empty] | Subtotal |  |  |  |  | 33277
| Note: number of uses per fixture for most fixtures based on LEED WEc3_2.2a.pdf water calculator |  |  |  | Contingency |  |  |  | 8% | 2662.16
| Spreadsheet inspired by multiple sources including USGBC/GBCI, EPA Watergy, and others |  |  |  | OH |  |  |  | 5% | 1663.85
[5 empty] | Profit |  |  |  | 10% | 3327.7
[5 empty] | Total |  |  |  |  | 40930.71
Note on D17: Jones, Perry/SAN: Unity factor to make all calcs looks same.
Note on E17: Jones, Perry/SAN: Unity factor to make all calcs looks same.
Note on I17: Jones, Perry/SAN: Duration of each showerhead reduced with large number of showers and lightly used locker rooms. Value represents total shower load of 30 mins/day=30/number of showerheads.
Note on J17: Jones, Perry/SAN: Unity factor to make all calcs looks same.
Note on K17: Jones, Perry/SAN: Unity factor to make all calcs looks same.

## 38-ElecGasWtrHtr
Replace Electric Hot Water Heater With Gas Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Existing example building had an electric water heater in a commercial kitchen. Assume 140 deg. F supply water required for commercial kitchen use. Assume power factor of 1 for resistance heating.
Conversion Factors: |  |  |  | Existing Water Heater Information |  |  |  |  | Assume 120o
1 deg F ∆T x 1 lb of water = |  | 1 | BTU | Volts | phase | amps | kW | capacity(g) | Supply Temperature
1 Gallon water = |  | 8.33 | lbs | 208 | 3 | 209 | 75 | 200 | ∆T | 60
1 BTU = |  | 1e-05 | Therms
1 therm = |  | 100000 | BTUs | Gallons/hour (GPH) |  | 400 | Hours/day | 12 | days/week | 5
Coversion of KWh to BTU |  | 3412 | Water temp. 140o |  | ∆T | 80 |  | Annual Gallons Used |  | 1248000
conversion of BTU to KWh: |  | 0.00029307
cost per kW: |  | 0.09 |  | Total BTU's/ year = ∆T x 8.33 lbs. / gallon x gallons used | [5 empty] | Total BTUs used /year
cost per therm: |  | 0.8 |  | kWh use per year = Total BTUs x 0.00029307
specific heat of water: |  | 1 |  | Therms / year = ( BTUs x .00001 therm/BTU)/ efficiency | [5 empty] | 831667200
Efficiency Electric Heat |  | 100%
Efficiency Gas |  | 95% |  |  | Fuel | kWh | Therms | Cost | Cost Savings
note: Sealed combustion gas unit. |  |  |  | Existing | Electric | 243737.5962 |  | 21936.3837
|  |  |  | Proposed | Gas |  | 8754.3916 | 7003.5133 | 14932.8704
[6 empty] | Cost from estimate worksheet |  |  | 14085.495
| Cost of energy saved per year: |  |  | 14932.8704 |  | Payback (years) |  |  | 0.94325
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Remove existing electric hot water heater. |  |  |  | ea | 1 | 5 | 150 | 15 | 170 | 170
Install piping for heater- assume 3/4" L copper |  |  |  | ln ft. | 15 | 6.5 | 7.5 | 0.2 | 14.2 | 213
Drill openings in exterior wall for flues, install, seal |  |  |  | ea | 2 | 35 | 200 | 15 | 250 | 500
Install new hot water heater |  |  |  | ea | 1 | 7000 | 1200 | 200 | 8400 | 8400
Wiring and control work, misc. as required. |  |  |  | ea | 1 | 300 | 800 | 45 | 1145 | 1145
Clean up |  |  |  | na | 6 | 0.4 | 0.5 | 0.05 | 0.95 | 5.7
[5 empty] | Subtotal |  |  |  | 9980.15 | 10433.7
[5 empty] | Contingency |  |  |  | 15% | 1565.055
[5 empty] | OH |  |  |  | 10% | 1043.37
[5 empty] | Profit |  |  |  | 10% | 1043.37
[5 empty] | Total |  |  |  |  | 14085.495

## 39-ElecGasKitchenEq
Convert Electric Kitchen Equipment to Gas Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Existing Kitchen Equipment is all electric in this example because there is no gas service to building. If gas was provided to the building from a nearby building which has gas service then the equipment could be changed to gas which would save energy cost. This could be done incrementally. The estimate of gas service costs upgrade not included in this worksheet.
1 Mcf = 1000cf gas |  | 1 therm = 100,000 BTUs |  | 1 CF gas = 1,025 BTU |  | 1 Mcf = 1.025 MBtu = 10.25 therms |  |  | $ per Mcf/1.025 = $ /MBtu
cost per kW: | 0.09 | cost per Mbtu: | 8 | cost per Mcf: | 8.2 | KWh to BTU's X | 3412.14 | Convert BTUs to KWh X |  | 0.00029307
Existing Kitchen Equipment |  | Est. Watts | 60% avg load. | hours/day | KWh | BTUs | MBTUs | Mcf Gas | $ Elec./ day | $ Gas/ day
5' Griddle |  | 22000 | 13200 | 12 | 158.4 | 540482.976 | 0.54048 | 0.554 | 14.256 | 4.5428
Range |  | 12000 | 7200 | 12 | 86.4 | 294808.896 | 0.29481 | 0.30218 | 7.776 | 2.4779
Fryer |  | 20000 | 12000 | 12 | 144 | 491348.16 | 0.49135 | 0.50363 | 12.96 | 4.1298
Ovens |  | 10000 | 6000 | 12 | 72 | 245674.08 | 0.24567 | 0.25182 | 6.48 | 2.0649
Totals |  | 64000 | 38400 | 48 | 460.8 | 1572314.112 | 1.5723 | 1.6116 | 41.472 | 13.2153
| Totals Per Year (assume 350 days) |  |  |  | 161280 | 550309939.2 | 550.3099 | 564.0677 | 14515.2 | 4625.355
Total Energy Savings (KWh) |  |  | 109887.1662 |  |  | Total Energy Savings / year |  |  | 9889.845

## 40-SprayValve
Replace Kitchen Pre-Rinse Spray Valve with Water Saving Model Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  | Washington DC |  |  | 2023-01-01
Older kitchen pre-rinse sprays are notorious for their inefficiency in water use. In addition to excess water use, hot water and the attendant energy use is wasted. Example proposes replacing an existing 20 year old pre rinse spray valve with new "Watersense" complient 1.25 GMP faucet
Conversion Factors: | [5 empty] | Gallons /Minute | Minutes/ day | Days / Year | Gallons / Year | ∆T
1 deg F ∆T x 1 lb of water 1 |  | 1 | BTU | Existing |  | 3.5 | 45 | 350 | 55125 | 60
1 Gallon water = |  | 8.33 | lbs | Proposed |  | 1.25 | 45 | 350 | 19687.5 | 60
1 BTU = |  | 1e-05 | Therms |  | BTUs/year =(gallons/year x ∆T x 8.33lbs/gallon)/Thermal Efficiency
1 therm = |  | 100000 | BTUs
Coversion of KWh to BTU |  | 3412 | Existing BTU's/year Gas: |  |  | 36735300 | Existing BTU's/year Electric: |  |  | 28113750
conversion of BTU to KWh: |  | 0.00029307 | Proposed BTU's/year Gas: |  |  | 13119750 | Proposed BTU's/year Electric: |  |  | 10040625
cost per kW: |  | 0.0937 |  | BTU Savings: |  | 23615550 |  | BTU Savings: |  | 18073125
cost per therm: |  | 0.8 |  | Therms Savings |  | 236.1555 |  | kWh Savings: |  | 5296.7101
Thermal Efficiency of Gas |  | 75% |  | Cost Savings |  | 188.9244 |  | Cost Savings |  | 496.3017
Thermal Efficiency of Electric. |  | 98%
Water Rate |  | 4 | kGal. | Gallons water savings: |  | 35437.5 |  | Cost of water saved: |  | 141.75
Current Hot Water Source: |  | electric
|  |  |  | hot water cost gas |  | 104.958 | HW cost electric |  | 275.7232
| KWh saved by changing spray valve: |  |  | 5296.7101 |  | Cost from estimate worksheet |  |  | 453.6675
| Cost of KW /yr + water saved per year: |  |  | 638.0517 |  | Payback (years) |  |  | 0.71102
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Remove Existing Pre-wash spray valve |  |  |  | ea | 1 | 4 | 10 | 1 | 15 | 15
Install new Pre-wash Spray valve |  |  |  | ea | 1 | 250 | 50 | 5 | 305 | 305
Clean up |  |  |  | na | 1 | 1 | 15 | 0.05 | 16.05 | 16.05
[5 empty] | Subtotal |  |  |  | 336.05 | 336.05
[5 empty] | Contingency |  |  |  | 15% | 50.4075
[5 empty] | OH |  |  |  | 10% | 33.605
[5 empty] | Profit |  |  |  | 10% | 33.605
[5 empty] | Total |  |  |  |  | 453.6675

## 41-KitchenHoodMakeup
Replace Kitchen Hood Exhaust System With Gas-fired Makeup Air Unit Payback
Building # | 1000 | Sample Building |  |  | Navy Base |  |  | Washington DC |  | 2023-01-01
Existing Kitchen Hood fan has no dedicated makeup air, so that it exhausts conditioned air whenever it runs. Proposed gas fired makup air fan provides makeup air at outdoor temperature until the temperature goes below 55 deg. F, at which point a 92% efficient gas-fired heater raises temperature to 55 Degrees setpoint. 90% maximum makup air ratio. (manufacturer recommendated settings).
1 Mcf = 1000cf gas |  | 1 therm = 100,000 BTUs |  | 1 CF gas = 1,025 BTU |  | 1 Mcf = 1.025 MBtu = 10.25 therms |  |  | $ per Mcf/1.025 = $ /MBtu
cost per kW: | 0.09 | cost per Mbtu: | 8 | cost per Mcf: | 8.2 | KWh to BTU's X | 3412.14 | Convert BTUs to KWh X |  | 0.00029307
Energy Loss From Conditioned Air Exhausted by Fan
Basic Formula for energy used to cool and heat air used by Fan in continuous use: BTU/yr = Fan CFM x specific heat of air (Btu/pound/deg f) x pounds of air / cubic foot x (HDD + CCD) x 60 min. x 24 hours (source - page 272 Guide To Energy Management) For CDDs multiply X 1/SHR to correct for Latent loads
Heating Degree Days @70: |  | 4988 | HDDs @55: |  | 2308 | Source: www.degreedays.net (temperature data from www.wunderground.com) National Airport |  | Sensible Heat Ratio (SHR)
Cooling Degree Days @ 76: |  | 415 | CDDs @ 88 |  | 0 |  |  | SHR = sensible heat/ total heat |  | 0.7
Exist. Exhaust Fan CFM: |  | 1800 | Specific Heat of Air |  | 0.24 | pounds dry air/ cu. ft. |  | 0.075 | 1/SHR | 1.4286
Hrs/ Day Hood operation |  | 14 | Minutes per hour |  | 60 | Prop. Ex Fan CFM: |  | 1500
Energy Used by Current Exhaust Fan | Heating season: |  | 135753408 |  | Energy Used by Proposed Exhaust Fan | Heating season: |  | 52345440 | Savings from new Exhaust Fan | 83407968
| Cooling season: |  | 16135200 |  |  | Cooling season: |  | 0 |  | 16135200
| Total: |  | 151888608 |  |  | Total: |  | 52345440 |  | 99543168
| KWh: |  | 44514.1569 |  |  | KWh: |  | 15340.9341 |  | 29173.2228
| Cost: |  | 4170.9765 |  |  | Cost: |  | 1437.4455 |  | 2733.531
[8 empty] | No Subsidy | Gas Subsidy | No Gas Cost
Total Energy Savings (KWh) |  |  | 29173.2228 |  | Total Implementation Cost |  |  | 30716.79 | 27286.5291 | 20322.06
Total Energy Savings ($) |  |  | 2733.531 |  | Payback (years) |  |  | 11.237 | 9.9822 | 7.4344
Estimated Cost of New Hood and Gas Fired Make-up air unit
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Remove existing 11' Hood, Exhaust Fan, and duct as required |  |  |  | ea | 1 | 25 | 1500 | 112 | 1637 | 1637
Install new 11' Hood |  |  |  | ea | 1 | 3200 | 1200 | 150 | 4550 | 4550
Install new Gas fired make-up unit |  |  |  | ea | 1 | 3200 | 2000 | 150 | 5350 | 5350
Pre-wired controls w/ heat sensor for interlock between exhaust fan, make-up air unit, and hood. |  |  |  | ea | 1 | 3000 | 550 | 30 | 3580 | 3580
Ansul Fire Suppression System |  |  |  | ea | 1 | 800 | 350 | 25 | 1175 | 1175
Clean up and testing. |  |  |  | LS | 1 | 25 | 200 | 5 | 230 | 230
[7 empty] | Subtotal |  | 27296.5113 | 16522
[7 empty] | Contingency |  | 8% | 1321.76
[7 empty] | OH |  | 5% | 826.1
[7 empty] | Profit |  | 10% | 1652.2
[7 empty] | Total |  |  | 20322.06
Estimated Cost of New Gas Service
Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
Dig trench from Building 1305 to building 1310 http://www.homewyse.com/services/cost_to_dig_trench.html |  |  |  | ln. ft | 180 | 0.2 | 7 | 5 | 12.2 | 2196
Place new gas pipe in trench (Means 33 51 10) |  |  |  | ln. ft | 180 | 7.5 | 5.5 | 0.75 | 13.75 | 2475
Backfill and compact, landscape with topsoil and seed |  |  |  | ln. ft | 180 | 7 | 6 | 8 | 21 | 3780
Connect piping at both buildings w/ necessary fittings |  |  |  | LS | 1 | 250 | 500 | 40 | 790 | 790
Clean up |  |  |  | ls | 1 | 50 | 400 | 300 | 750 | 750
[7 empty] | Subtotal |  | 46.95 | 8451
Typically the gas supplier (Washington Gas) will subsidize the cost of new gas service based on demand. Gas service will allow existing electric kitchen appliances to be replaced with more efficient gas ones as noted in this report. | [6 empty] | Contingency |  | 8% | 676.08
[7 empty] | OH |  | 5% | 422.55
[7 empty] | Profit |  | 10% | 845.1
[7 empty] | Total |  |  | 10394.73
[7 empty] | Assumed Gas subsidy |  | 33% | 6964.4691

## 42-IndoorCondenser
Move Indoor Condenser Outside Payback
Building # |  | 1000 | Sample Building |  | Navy Base |  |  | Washington DC |  |  | 2023-01-01
Calculations are based on moving BTUs used in the refrigeration cycle from inside the pantry storage area to the exterior of the building during the cooling months. Note - if moving condenser outside is not possible, consider installing a ducted exhaust system
| Size of Cooler ( 12 x 20) |  | 16633 | CF |  | Months of Unwanted Heat Gain |  |  |  |  | 8
| BTU per hour |  | 16633 | See Reference |  | Average days per month |  |  |  |  | 30
| Amount of BTUs per year |  | 95806080 |  |  | Hours per day |  |  |  |  | 24
| KWh per year |  | 28077.9904 |  |  | Cost of KWh per year |  |  |  |  | 2630.9077
|  | Source: | https://www.heatcraftrpd.com/PDF/MQuick%20Load%20Calculations.pdf
|  | Energy Saved |  |  | 28077.9904 |  | Cost from estimate worksheet |  |  | 12737.25
|  | Cost of energy saved per year: |  |  | 2630.9077 |  | Payback (years) |  |  | 4.8414
| Description |  |  |  | unit | QTY | material per unit | labor per unit | Equipment Per Unit | total per unit | Total
| Build duct and fan -OR- relocate refrigeration system to outside |  |  |  | ea | 1 | 4000 | 5000 | 250 | 9250 | 9250
| Clean up |  |  |  | ea | 1 | 20 | 150 | 15 | 185 | 185
[6 empty] | Subtotal |  |  |  | 9435 | 9435
[6 empty] | Contingency |  |  |  | 15% | 1415.25
[6 empty] | OH |  |  |  | 10% | 943.5
[6 empty] | Profit |  |  |  | 10% | 943.5
[6 empty] | Total |  |  |  |  | 12737.25