## 2 (hidden)
Change Log/Notes:
Change Date | Change Location | Change Made | POC
2016-09-26 | all SZ tabs | added SA-T-SP, SF-C, SF-C-MIN points | Brian Clark
2016-09-26 | all DD/MZ tabs | added ZN-D-SP, ZN-D-C-EFF, SF-C, SF-C-MIN points | Brian Clark
2016-09-26 | VAV AHU tab | added SF/RF-C-MIN points and DSPR points: ZN-D-C-EFF, ZN-D-C-MIN/MAX, SA-P-SP-RT, and reset to SA-P-SP | Brian Clark
2016-09-26 | all SZ, DD/MZ, VAV AHUs | added optional DCV points: ZN-CO2, ZN-CO2-EFF, ZN-CO2-MIN/MAX, MINOA-F-MIN/MAX | Brian Clark
2016-09-26 | VAV terminal units | added optional DCV points: ZN-CO2, ZN-CO2-MIN/MAX, VAV-SA-F-MIN1/2 | Brian Clark

## Introduction and Notes
Points Schedule Introduction:
1 | The Points Schedule is a required design and as-built document per UFC 3-410-02. Typically the first draft is provided in the 65% design submittal.
2 | These Points Schedules are templates to be used as a starting point for designers. These templates meet the requirements outlined in UFC 3-410-02 DDC for HVAC and other Building Control Systems.
3 | The templates are not intended to be the final points schedule for a project. The formatting can be the same but every project is different, with differing designs and project requirements that will require different inputs.
4 | The Points Schedule process is started by the designer and provided as a part of the design. Coordination with the installation or building owner is required to develop a Points Schedule that will meet their needs.
5 | The controls contractor/installer will complete the points schedule and will provide it as a part of the as-built drawings.
6 | The Index tab provides the tab number with it's cooresponding system type.
See UFC 3-410-02 Appendix D for detailed information on the Points Schedules
In general:
The controls contractor is responsible for submitting a completed points schedule.
The points schedule uses brackets and symbology to provide clarity
|  | Symbol |  | Meaning
|  | [___] |  | “Square brackets” (“[___]”) are used to indicate selections or entries made by the designer
|  | <___> |  | “Angle brackets” (“<___>”) are used to indicate selections or entries that must be made by the building control system contractor.
|  | ~ |  | A tilde (“~”) is used in a cell where there could be a valid entry, but no entry is required (i.e. it’s specifically used to mean “I could have put a value here but I chose not to enter one”)
|  |  | or N/A | An “N/A” (or a greyed out cell, or a combination of N/A and a greyed out cell) is used when there is no possibility of a valid entry for that particular cell.

## Index
Worksheet TAB | Description
Notes | Notes
Index | Index
3 | ALL AIR SMALL PACKAGE UNITARY SYSTEM
4 | HEATING AND VENTILATING UNIT
5 | SINGLE ZONE WITH HEATING AND DX COILS
6 | SINGLE ZONE WITH HEATING AND COOLING COILS
7 | SINGLE ZONE WITH DUAL TEMPERATURE COIL
8 | SINGLE ZONE WITH HEATING AND COOLING COILS AND RETURN AIR BYPASS
9 | SINGLE ZONE WITH HUMIDITY CONTROL
10 | DUAL DUCT WITH RETURN FAN
11 | MULTIZONE WITH RETURN FAN
12 | MULTIZONE WITH HOT DECK BYPASS AND RETURN FAN
13 | VAV WITH RETURN FAN
" | VAV BOXES
14 | TERMINAL AND ZONE UNITS (UNIT HEATER, PERIM RADIATION, FAN COIL UNIT)
15 | HYDRONIC HEATING HOT WATER FROM DISTRIBUTED STEAM CONVERTER
16 | HIGH TEMPERATURE HOT WATER/HOT WATER HEAT EXCHANGER
17 | HOT WATER BOILER WITH CONSTANT AND NON-CONSTANT BOILER LOOP
18 | STEAM/HOT WATER CONVERTER DUAL TEMPERATURE SYSTEM
19 | HTHW/HOT WATER HEAT EXCHANGER DUAL TEMPERATURE SYSTEM
20 | SECONDARY HYDRONIC WITH CONSTANT SPEED PUMPING
21 | SECONDARY HYDRONIC WITH VARIABLE SPEED PUMPING
22 | ELECTRIC METER
23 | GAS METER
24 | WATER METER
25 | SWITCHGEAR
26 | SUBSTATION
27 | TRANSFORMER
28 | LIFT STATION
29 | DOMESTIC HOT WATER BOILER
30 | HOT WATER BOILER
31 | SOLAR HOT WATER
32 | CHILLED WATER THERMAL STORAGE SYSTEM
33 | WATER COOLED CENTRIFUGAL CHILLER INTERFACE
34 | AIR COOLED CENTRIFUGAL CHILLER INTERFACE
35 | GENERATOR
36 | DEDICATED OUTSIDE AIR UNIT
37 | CHILLED WATER PLANT

## 3
UNITARY SYSTEM: PACKAGED AC OR SPLIT SYSTEM [WITH HEAT] [WITH HEAT PUMP]
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  |  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  |  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  |  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  |  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
| FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
| PROOFS & SAFETIES |  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) | <___> | <___> | ALM/NORMAL | <BI> |  | C |  |  |  | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___> | <___> | <___> | <___>
|  | RST-BUT | SYSTEM RESET BUTTON | <___> |  |  | [___] |  |  | [ ~ ][VO] | [5 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
| START/STOP | MODE-SEL | HEAT-OFF-COOL MODE SELECTION SWITCH INPUT | <___> |  | HEAT/OFF/COOL/ <EMERG> | <___> |  |  | [ ~ ] | [ ~ ] | [ ~ ] | [ ~ ] |  | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | SYS-OCC | OCCUPANCY INPUT (FROM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | <___> |  | OCC/UNOCC | BI |  |  | [ V ] | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | SF-SEL | SUPPLY FAN ON/AUTO SELECT SWITCH | <___> |  | ON/AUTO | BI |  |  | [ ~ ] | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | UNIT STATUS | UNIT STATUS (SEE NOTES) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | HVAC_STATUS | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ECONOMIZER | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___]
|  | OA-D-C | OUTSIDE AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO |  |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___]
|  | ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT | <___> | [___] | <___> |  |  | OC | VO | [ ~ ] | [ ~ ]
|  | ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT | <___> | [___] | <___> |  |  | OC | VO | [ ~ ] | [ ~ ]
| ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T MORE THAN 77 DEG F OR BELOW 68 DEG F | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | ZN-T-SP | ZONE TEMPERATURE SETPOINT | <___> | OCCUPANT ADJUSTABLE | [68-77 DEG F] | AI |  | C | VO | [ ~ ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCC MODE | <___> | [68 DEG F FOR HEATING, 78 DEG F FOR COOLING] | [ ~ ] |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | SF-SS | SUPPLY FAN START/STOP COMMAND | <___> |  | ON/OFF | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | COMP-MODE | COMPRESSOR COOLING/HEATING MODE | <___> |  | CLG/HTG | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | COMP-SS | COMPRESSOR START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | EMERG-HTG-2P | EMERG HEATING COMMAND (2-POS) | <___> | ~ | ON/OFF | AO | [~] | H | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | HEATING VALVE CONTROL LOOP CONFIGURATION SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | COOLING VALVE CONTROL LOOP CONFIGURATION SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
Notes:
|  |  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM (IF APPLICABLE)
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 4
HEATING AND VENTILATING UNIT (UNIT VENTILATOR)
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | HTG-DA-T-LL | HEATING COIL DISCHARGE TEMPERATURE LOW LIMIT SWITCH | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H |  |  |  | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H |  |  |  | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H |  |  |  | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | [5 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
| SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [V] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT | <___> | [55 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | [~] | [~] |  | VO | [V] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [V] | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | HVAC_STATUS | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | <___> | [OCC ADJ] | [68-77 DEG F] | AI |  |  | VO | [V] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-V-C | HEATING COIL VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [V] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OA-D-C | OUTSIDE AIR DAMPER COMMAND | <___> |  | <0-100% OPEN> | AO | [~] |  | VO | [V] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OA-D-MIN | OUTSIDE AIR DAMPER MINIMUM POSITION | <___> | [ ___ ] [% OPEN] |  | AO | [8 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| HEATING VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| OUTSIDE AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI | [5 empty] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 5
SINGLE ZONE WITH HEATING AND DX COILS
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [V] | ~ | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HTG-DA-T-LL | HEATING COIL DISCHARGE TEMPERATURE LOW LIMIT SWITCH | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [~] | [~] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT |  | [55 DEG F] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | V | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | HVAC_STATUS | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
SUPPLY FAN CAPACITY CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | [6 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
MINIMUM OUTSIDE AIRFLOW | MINOA-D-C | MINIMUM OUTSIDE AIR DAMPER COMMAND | <___> |  | OPEN/CLOSED | BO | [~] |  | VO | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINOA-F | MINIMUM OUTSIDE AIR FLOW SETTING |  | [____ CFM] |  |  |  | C | [6 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
ZONE TEMPERATURE CONTROL: MA DAMPERS HEATING COIL COOLING COIL | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | [7 empty] | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| MIXED AIR PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | 0 | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [V[O]] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | 0 | <___> | <___> |  |  |  | <___>
| HTG-V-C | HEATING COIL VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [V] | [X] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | 0 | <___> | <___> | <___> | 0 | <___> | <___>
| DX-V-C | DX UNIT COMMAND | <___> |  | ON/OFF | BO | [~] |  | VO | [V] | [X] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-T-SP | SUPPLY AIR TEMPERATURE SET POINT |  | [ RESET ] | <55-80 DEG F> |  |  | C | V | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [~] | [~] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OPTIONAL DCV POINTS | ZN-CO2 | ZONE CO2 | <___> |  | <___> | AI |  |  | V | V | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | V | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | V | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MA-D-C-MIN1 | MINIMUM DAMPER COMMAND 1 (DESIGN MIN OUTSIDE AIR) |  | [____ CFM] |  |  |  | C | VO | V | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MA-D-C-MIN2 | MINIMUM DAMPER COMMAND 2 (SF-ONLY BASED OUTSIDE AIR) |  | [____ CFM] |  |  |  | C | VO | V | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 6
SINGLE ZONE WITH HEATING AND COOLING COILS
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  |  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  |  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  |  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  |  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
| FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
| PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [V] | [~] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | HTG-DA-T-LL | HEATING COIL DISCHARGE TEMPERATURE LOW LIMIT SWITCH | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [~] | [~] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT |  | [55 DEG F] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [V] | [~] | ~ | [INFO] [CRIT] | [___] | MSV <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [V] | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | HVAC_STATUS | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[16 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[16 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | <___> |  | OPEN/CLOSED | BO | [~] |  | VO | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETTING |  | [____ CFM] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[16 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[16 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| ZONE TEMPERATURE CONTROL: MA DAMPERS HEATING COIL COOLING COIL | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | [7 empty] | <___>
|  | MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
|  | ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-78 DEG F] | AI |  | C | VO | [V[O]] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | HTG-V-C | HEATING COIL VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | CLG-V-C | COOLING COIL VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | MIXED AIR PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | HEATING VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | COOLING VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  |  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | SA-T-SP | SUPPLY AIR TEMPERATURE SET POINT |  | [ RESET ] | <55-80 DEG F> |  |  | C | V | [V] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [V] | [~] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
`
| OPTIONAL DCV POINTS | ZN-CO2 | ZONE CO2 | <___> |  | <___> | AI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | MINOA-D-MAX | MINIMUM OUTSIDE AIR MAXIMUM DAMPER POSITION |  | [____ CFM] <____ %> |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
|  | MINOA-D-MIN | MINIMUM OUTSIDE AIR MINIMUM DAMPER POSITION |  | [____ CFM] <____ %> |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>
|  |  |  | 7) | MINOA-D-MAX AND MINOA-D-MIN: CONTRACTOR DOCUMENTS THE PERCENT DAMPER POSTION AT THE DESIGNER SPECIFIED CFM

## 7
SINGLE ZONE WITH DUAL TEMPERATURE COIL
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DT-DA-T-LL | DUAL TEMP COIL DISCHARGE AIR TEMP LOW LIMIT SWITCH | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT |  | [55 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | MSV <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | HVAC_STATUS | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | <___> |  | OPEN/CLOSED | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETTING |  | [____ CFM] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
ZONE TEMPERATURE CONTROL: MA DAMPERS HEATING COIL COOLING COIL | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | [7 empty] | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| DTWS-T | DUAL TEMP WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DTWS-T-SP | DUAL TEMP WATER SUPPLY TEMPERATURE SETPOINT |  |  | <___> | AI |  |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DT-V-C | DUAL TEMP COIL VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MIXED AIR PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| DUAL TEMP COIL VALVE PID LOOP SETTINGS FOR COOLING | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| DUAL TEMP COIL VALVE PID LOOP SETTINGS FOR HEATING | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[27 empty] | 0 | <___>
[27 empty] | 0 | <___>
OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-T-SP | SUPPLY AIR TEMPERATURE SET POINT |  | [ RESET ] | <55-80 DEG F> |  |  | C | V | [V] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [V] | [~] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OPTIONAL DCV POINTS | ZN-CO2 | ZONE CO2 | <___> |  | <___> | AI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-D-MAX | MINIMUM OUTSIDE AIR MAXIMUM DAMPER POSITION |  | [____ CFM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-D-MIN | MINIMUM OUTSIDE AIR MINIMUM DAMPER POSITION |  | [____ CFM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 8
SINGLE ZONE WITH HEATING AND COOLING COILS AND RETURN AIR BYPASS
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
|  |  | 16777215 | [8 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HTG-DA-T-LL | HEATING COIL DISCHARGE TEMPERATURE LOW LIMIT SWITCH | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT |  | [55 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | MSV <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | HVAC_STATUS | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | <___> |  | OPEN/CLOSED | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETTING |  | [____ CFM] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
ZONE TEMPERATURE CONTROL: MA DAMPERS HEATING COIL COOLING COIL BYPASS DAMPER | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | [7 empty] | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
| ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | V | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | V | X |  |  |  | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-V-C | HEATING COIL VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | V | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CLG-V-C-2P | COOLING COIL VALVE COMMAND (2-POS) | <___> |  | OPEN/CLOSED | BO | [~] |  | VO | V | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BA-D-C | BYPASS AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | V | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MIXED AIR PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| BYPASS DAMPER PID LOOP SETTINGS FOR COOLING | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| HEATING VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
<___>
<___>
OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-T-SP | SUPPLY AIR TEMPERATURE SET POINT |  | [ RESET ] | <55-80 DEG F> |  |  | C | V | [V] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [V] | [~] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BA-FLT-P-HL | BYPASS AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [V] | [~] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OPTIONAL DCV POINTS | ZN-CO2 | ZONE CO2 | <___> |  | <___> | AI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-D-MAX | MINIMUM OUTSIDE AIR MAXIMUM DAMPER POSITION |  | [____ CFM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-D-MIN | MINIMUM OUTSIDE AIR MINIMUM DAMPER POSITION |  | [____ CFM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>
1

## 9
SINGLE ZONE WITH HUMIDITY CONTROL | [9 empty] | #NAME? | #NAME? | #NAME? | #NAME?
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [14 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [14 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [14 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [14 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[14 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD |  | TREND REQ'D |  | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] |  | [ ~ ] |  | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PH-DA-T-LL | PREHEAT COIL DISCHARGE AIR TEMP LOW LIMIT SWITCH | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ |  | ~ |  | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ |  | ~ |  | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ |  | ~ |  | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ |  | ~ |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] |  | [ ~ ] |  | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT |  | [55 DEG F] |  |  |  | C | VO | [ ~ ] |  | [ ~ ] |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] |  | [ ~ ] |  | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] |  | [ ~ ] |  | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] |  | [ ~ ] |  | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] |  | X |  | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [~] |  | [~] |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[17 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[17 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | <___> |  | OPEN/CLOSED | BO | [~] |  | VO | [ ~ ] |  | [ ~ ] |  | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETTING |  | [____ CFM] |  |  |  | C | ~ | ~ |  | ~ |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[17 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[17 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
PREHEAT COIL CONTROL | PH-DA-T | PREHEAT COIL DISCHARGE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] |  | X |  | PH-DA-T IS MORE THAN 34 DEG F BELOW PH-DA-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| PH-DA-T-SP | PREHEAT COIL DISCHARGE AIR TEMPERATURE SETPOINT |  | [___] |  |  |  | C | VO | [ V ] |  | X |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| PH-V-C | PREHEAT COIL VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] |  | [ X ] |  | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PREHEAT COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [21 empty] | <___>
ZONE TEMPERATURE AND HUMIDITY CONTROL | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] |  | X |  | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] |  | X |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-RH | ZONE RELATIVE HUMIDITY | <___> |  | <0 - 100 % RH> | AI |  |  | V | [ V ] |  | X |  | ** ZN-RH IS MORE THAN 10% ABOVE OR BELOW ZN-RH-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-RH-SP | ZONE RELATIVE HUMIDITY SETPOINT |  |  | <___> | AI |  | C | ~ | ~ |  | X |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SA-RH | SUPPLY AIR RELATIVE HUMIDITY | <___> |  | <0 - 100 % RH> | AI |  |  | V | [ V ] |  | X |  | SA-RH IS ABOVE 90% RH | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-RH-SP | SUPPLY AIR RELATIVE HUMIDITY SETPOINT |  | 80% RH | <___> | AI |  | C | ~ | ~ |  | ~ |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| RH-V-C | REHEAT COIL VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] |  | [ X ] |  | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CLG-V-C | COOLING COIL VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] |  | [ X ] |  | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HUM-V-C | HUMIDIFIER VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] |  | [ X ] |  | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING COIL VALVE PID LOOP SETTINGS FOR RH CONTROL | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [21 empty] | <___>
| COOLING COIL VALVE PID LOOP SETTINGS FOR TEMP CONTROL | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [21 empty] | <___>
| HEATING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [21 empty] | <___>
| HUMIDIFIER VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [21 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [21 empty] | <___>
<___>
<___>
OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] |  | [~] |  | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-T-SP | SUPPLY AIR TEMPERATURE SET POINT |  | [ RESET ] | <55-80 DEG F> |  |  | C | V | [V] |  | X |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [V] |  | [~] |  | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OA-FLT-P-HL | OUTSIDE AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [V] |  | [~] |  | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OPTIONAL DCV POINTS | ZN-CO2 | ZONE CO2 | <___> |  | <___> | AI |  |  | V | [V] |  | X |  | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [V] |  | [~] |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [V] |  | [~] |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-D-MAX | MINIMUM OUTSIDE AIR MAXIMUM DAMPER POSITION |  | [____ CFM] |  |  |  | C | VO | [V] |  | [~] |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-D-MIN | MINIMUM OUTSIDE AIR MINIMUM DAMPER POSITION |  | [____ CFM] |  |  |  | C | VO | [V] |  | [~] |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 11
MULTIZONE WITH RETURN FAN
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RF-S | RETURN FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-LL | MIXED AIR TEMPERATURE LOW LIMIT | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT |  | [55 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
RETURN FAN CONTROL | RF-C | RETURN FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| RF-C-MIN | RETURN FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| F-DIFF-SP | FLOW DIFFERENCE SETPOINT |  | [___ CFM] | [0 - ___ CFM] | AO | [~] | C | [6 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | <___> |  | OPEN/CLOSED | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___> | <___> | <___> | <___>
| MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETTING |  | [____ CFM] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
MIXED AIR TEMPERATURE CONTROL WITH ECONOMIZER | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T | MIXED AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT |  | [___] | <___> |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MIXED AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
<___>
HOT DECK CONTROL | HD-T | HOT DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HD-T-SP | HOT DECK TEMPERATURE SETPOINT |  | [ RESET ] | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HD-V-C | HOT DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HEATING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
COLD DECK CONTROL | CD-T | COLD DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CD-T-SP | COLD DECK TEMPERATURE SETPOINT |  |  | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| CD-V-C | COLD DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
ZONE [1] TEMPERATURE CONTROL | ZN(1)-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN(1)-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN(1)-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
ZONE [2] TEMPERATURE CONTROL | ZN(2)-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN(2)-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN(2)-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
OTHER POINTS | ZN-D-SP | ZONE DAMPER COMMAND SETPOINT |  | [95%] |  |  |  | C | VO | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-C-EFF | MAXIMUM (EFFECTIVE) ZONE DAMPER COMMAND |  |  | 0-100% OPEN |  |  |  | V | V | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-T | RETURN AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [ ~ ] | [ ~ ] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OPTIONAL DCV POINTS | ZN-CO2-EFF | MAXIMUM ZONE CO2 | <___> |  | <___> | AI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MAX | MINIMUM OUTSIDE AIR FLOW MAXIMUM SETPOINT |  | [____ CFM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW MINIMUM SETPOINT |  | [____ CFM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 10
DUAL DUCT WITH RETURN FAN
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RF-S | RETURN FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-LL | MIXED AIR TEMPERATURE LOW LIMIT | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT |  | [55 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
RETURN FAN CONTROL | RF-C | RETURN FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| RF-C-MIN | RETURN FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| F-DIFF-SP | FLOW DIFFERENCE SETPOINT |  | [___ CFM] | [0 - ___ CFM] | AO | [~] | C | [6 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | <___> |  | OPEN/CLOSED | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETTING |  | [____ CFM] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
MIXED AIR TEMPERATURE CONTROL WITH ECONOMIZER | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T | MIXED AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT |  | [___] | <___> |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MIXED AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
HOT DECK CONTROL | HD-T | HOT DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HD-T-SP | HOT DECK TEMPERATURE SETPOINT |  | [ RESET ] | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HD-V-C | HOT DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HEATING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
COLD DECK CONTROL | CD-T | COLD DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CD-T-SP | COLD DECK TEMPERATURE SETPOINT |  |  | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| CD-V-C | COLD DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
<___>
ZONE [1] TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
<___>
ZONE [2] TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
<___>
| ZN-D-SP | ZONE DAMPER COMMAND SETPOINT |  | [95%] |  |  |  | C | VO | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
OTHER POINTS | ZN-D-C-EFF | MAXIMUM (EFFECTIVE) ZONE DAMPER COMMAND |  |  | 0-100% OPEN |  |  |  | V | V | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-T | RETURN AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [ ~ ] | [ ~ ] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OPTIONAL DCV POINTS | ZN-CO2-EFF | MAXIMUM ZONE CO2 | <___> |  | <___> | AI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MAX | MINIMUM OUTSIDE AIR FLOW MAXIMUM SETPOINT |  | [____ CFM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW MINIMUM SETPOINT |  | [____ CFM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 12
MULTIZONE WITH HOT DECK BYPASS WITH RETURN FAN
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RF-S | RETURN FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-LL | MIXED AIR TEMPERATURE LOW LIMIT | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT |  | [55 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
RETURN FAN CONTROL | RF-C | RETURN FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| RF-C-MIN | RETURN FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| F-DIFF-SP | FLOW DIFFERENCE SETPOINT |  | [___ CFM] | [0 - ___ CFM] | AO | [~] | C | [6 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | <___> |  | OPEN/CLOSED | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETTING |  | [____ CFM] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
MIXED AIR TEMPERATURE CONTROL WITH ECONOMIZER | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T | MIXED AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT |  | [___] | <___> |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MIXED AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
COLD DECK CONTROL | CD-T | COLD DECK TEMPERATURE | <___> |  | 0-100% OPEN | AO | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CD-T-SP | COLD DECK TEMPERATURE SETPOINT |  |  | <___> | AI |  |  | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| CD-V-C | COLD DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
ZONE [1] TEMPERATURE CONTROL | ZN(1)-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  | <___> | <___> | <___> | <___>
| ZN(1)-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN(1)-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN(1)-[V][HTG-C | VAV <REHEAT VALVE> <HEAT ELEMENT> COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| VAV [VALVE][ELEMENT] PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
ZONE [2] TEMPERATURE CONTROL | ZN(2)-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN(2)-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN(2)-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN(2)-[V][HTG-C | VAV <REHEAT VALVE> <HEAT ELEMENT> COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [12 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | <____> | <___> | <___> |  |  |  | C | [12 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV [VALVE][ELEMENT] PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
<___>
OTHER POINTS | ZN-D-SP | ZONE DAMPER COMMAND SETPOINT |  | [95%] |  |  |  | C | VO | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-C-EFF | MAXIMUM (EFFECTIVE) ZONE DAMPER COMMAND |  |  | 0-100% OPEN |  |  |  | V | V | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-T | RETURN AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [ ~ ] | [ ~ ] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OPTIONAL DCV POINTS | ZN-CO2-EFF | MAXIMUM ZONE CO2 | <___> |  | <___> | AI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MAX | MINIMUM OUTSIDE AIR FLOW MAXIMUM SETPOINT |  | [____ CFM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW MINIMUM SETPOINT |  | [____ CFM] |  |  |  | C | VO | [V] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 13
VAV [WITH][WITHOUT] RETURN FAN
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [13 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [13 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [13 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [13 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD |  | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] |  | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | <___> | <___> | <___> | <___>
| RF-S | RETURN FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] |  | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ |  | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ |  | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CLG-DA-T-LL | COOLING COIL DISCHARGE TEMPERATURE LOW LIMIT SWITCH | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ |  | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-P-HL | SUPPLY AIR PRESSURE HIGH LIMIT | <___> | [___] IWC | ALM/NORMAL | BI |  |  | ~ | ~ |  | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ |  | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] |  | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT |  | [55 DEG F] |  |  |  | C | VO | [ ~ ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] |  | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] |  | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] |  | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
SUPPLY FAN CAPACITY CONTROL | SA-P | SUPPLY AIR PRESSURE | <___> |  | <___> | AI |  |  | V | [ V ] |  | X | *SA-P MORE THAN 20% ABOVE OR BELOW SA-P-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-P-SP | SUPPLY AIR PRESSURE SETPOINT |  | [ RESET ] | <___> |  |  | C | VO | [ V ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SA-P-SP-RT | SUPPLY AIR PRESSURE SETPOINT RATE OF CHANGE |  | [ 0.01 ] | " w.c./min |  |  | C | V | [ V ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [ ~ ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [ V ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| SUPPLY FAN PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [20 empty] | <___>
[16 empty] | <___> | <___> | <___> | <___> | <___> | <___>
RETURN FAN CAPACITY CONTROL | SA-F | SUPPLY AIR FLOW | <___> | [___ CFM] | [0 - ___ CFM] | AI |  |  | V | [ V ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-F | RETURN AIR FLOW | <___> | [___ CFM] | [0 - ___ CFM] | AI |  |  | V | [ V ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| F-DIFF-SP | FLOW DIFFERENCE SETPOINT |  | [___ CFM] | [0 - ___ CFM] | AO | [~] | C | VO | [ ~ ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| RF-C | RETURN FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RF-C-MIN | RETURN FAN COMMAND MINIMUM |  | [25%] |  |  |  | C | VO | [ V ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| RETURN FAN PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [20 empty] | <___>
MINIMUM OUTSIDE AIR | OA-F | OUTSIDE AIR FLOW | <___> | [___ CFM] | [0 - ___ CFM] | AI |  |  | V | [ V ] |  | X | MINOA-F LESS THAN 80% OF MINOA-F-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETPOINT (SETTING) |  | [____ CFM] |  |  |  | C | VO | [ V ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-D-C | MINIMUM OUTSIDE AIR DAMPER COMMAND | <___> |  | OPEN/CLOSED | BO | [~] |  | VO | [ V ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINIMUM OUTSIDE AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [20 empty] | <___>
MIXED AIR TEMPERATURE CONTROL WITH ECONOMIZER | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] |  | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T | MIXED AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] |  | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT |  | [___] | <___> |  |  | C | VO | [ V ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MIXED AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [20 empty] | <___>
[16 empty] | <___> | <___> | <___> | <___> | <___> | <___>
SUPPLY AIR TEMPERATURE | SA-T | SUPPLY AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] |  | X | *SA-T MORE THAN 10 DEG F ABOVE OR BELOW SETPOINT | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-T-SP | SUPPLY AIR TEMPERATURE SETPOINT |  | [55 DEG F] | <___> |  |  | C | VO | [ V ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-V-C | COOLING VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [20 empty] | <___>
OTHER POINTS | RA-T | RETURN AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-D-C-MAX | ZONE DAMPER COMMAND SETPOINT MAXIMUM |  | [90%] |  |  |  | C | VO | [V] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-C-MIN | ZONE DAMPER COMMAND SETPOINT MINIMUM |  | [50%] |  |  |  | C | VO | [V] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-C-EFF | MAXIMUM (EFFECTIVE) ZONE DAMPER COMMAND |  |  | 0-100% OPEN |  |  |  | V | [V] |  | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [ ~ ] | [ ~ ] | [ ~ ] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OA-FLT-P-HL | OUTSIDE AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [ ~ ] | [ ~ ] | [ ~ ] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OPTIONAL DCV POINTS | ZN-CO2-EFF | MAXIMUM ZONE CO2 | <___> |  | <___> | AI |  |  | V | [V] |  | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MAX | MINIMUM OUTSIDE AIR FLOW MAXIMUM SETPOINT |  | [____ CFM] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW MINIMUM SETPOINT |  | [____ CFM] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>
COOLING ONLY VAV BOX
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD |  | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES |  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | [ ~ ] | [ ~ ] |  | [ ~ ] | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | [ ~ ] | [ ~ ] |  | [ ~ ] | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | VO | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | MSV <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | <___> |  | <___> | BI |  |  | [ ~ ] | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | MSV <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| EFF-OCC | EFFECTIVE OCCUPANCY | <___> |  | <___> | NET-OUT |  |  | V | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | MSV <___> | <___> | OCCUPANCY | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] |  | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV-SA-F | VAV SUPPLY AIR FLOW | <___> | [___ CFM] | [0 - ___ CFM] | AI |  |  | V | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV-SA-F-SP | VAV SUPPLY AIR FLOW SETPOINT |  | RESET SCHED | [0 - ___ CFM] |  |  | C | [ ~ ] | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV-D-C | VAV DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | V | [ ~ ] |  | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [13 empty] | <___> | <___> | <___> |  |  |  |  | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [13 empty] | <___> | <___> | <___> |  |  |  |  | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [13 empty] | <___> | <___> | <___> |  |  |  |  | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [13 empty] | <___> | <___> | <___> |  |  |  |  | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [13 empty] | <___> | <___> | <___> |  |  |  |  | <___>
|  | <____> | <___> | <___> |  |  |  | C | [13 empty] | <___> | <___> | <___> |  |  |  |  | <___>
[16 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
Notes:
|  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  | 3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
|  | 4) | ALARM CONDITIONS MARKED WITH A DOUBLE ASTERISK (**) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN 30 MINUTES.
|  | 5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
VAV BOX WITH REHEAT
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD |  | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES |  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ |  | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ |  | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | VO | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | MSV <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | <___> |  | <___> | BI |  |  | [ ~ ] | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | MSV <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| EFF-OCC | EFFECTIVE OCCUPANCY | <___> |  | <___> | NET-OUT |  |  | V | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | MSV <___> | <___> | OCCUPANCY | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | HVAC_COOL/ HVAC_HEAT/ HVAC_OFF | NET-OUT |  |  | [ V ] | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | HVAC_STATUS | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] |  | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ ~ ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE |  | [ 82 DEG F ] | <___> | AI |  | C | [ ~ ] | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV-SA-F | VAV SUPPLY AIR FLOW | <___> | [___ CFM] | [0 - ___ CFM] | AI |  |  | V | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV-SA-F-SP | VAV SUPPLY AIR FLOW SETPOINT |  | RESET SCHED | [0 - ___ CFM] |  |  | C | [ ~ ] | [ ~ ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| VAV-D-C | VAV DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | V | [ ~ ] |  | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV-V-C | VAV <REHEAT VALVE> <HEAT ELEMENT> COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | V | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | ZONE TEMPERATURE SETPOINT DEADBAND |  | RESET SCHED | [0 - ___ CFM] |  |  | C | ~ | ~ |  | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| VAV DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [20 empty] | <___>
| VAV VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [20 empty] | <___>
[27 empty] | 0 | 0 | <___>
OTHER POINTS | VAV-DA-T | VAV DISCHARGE AIR TEMPERATURE | <___> |  | 0-100% OPEN | AO | [~] |  | V | [ ~ ] |  | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  | <___> | <___> | <___> | <___> | <___>
OPTIONAL DCV POINTS | ZN-CO2 | ZONE CO2 | <___> |  | <___> | AI |  |  | V | [V] |  | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> |  |  |  | <___>
| VAV-SA-F-MIN1 | VAV SUPPLY AIR FLOW MINIMUM 1 (DESIGN MINIMUM) |  | [____ CFM] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> |  |  |  | <___>
| VAV-SA-F-MIN2 | VAV SUPPLY AIR FLOW MINIMUM 2 ( SF-ONLY MINIMUM) |  | [____ CFM] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> |  |  |  | <___>
Notes:
|  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  | 3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
|  | 4) | ALARM CONDITIONS MARKED WITH A DOUBLE ASTERISK (**) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN 30 MINUTES.
|  | 5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
SERIES FAN POWERED VAV BOX [WITH REHEAT]
AND
PARALLEL FAN POWERED VAV BOX [WITH REHEAT]
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD |  | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES |  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ |  | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ |  | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | VO | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | MSV <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | <___> |  | <___> | BI |  |  | [ ~ ] | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | MSV <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| EFF-OCC | EFFECTIVE OCCUPANCY | <___> |  | <___> | NET-OUT |  |  | V | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | MSV <___> | <___> | OCCUPANCY | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | HVAC_COOL/ HVAC_HEAT/ HVAC_OFF | NET-OUT |  |  | [ V ] | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | HVAC_STATUS | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] |  | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ ~ ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE | <___> | [ 82 DEG F ] | <___> | AI |  | C | [ ~ ] | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV-SA-F | VAV SUPPLY AIR FLOW | <___> | [___ CFM] | [0 - ___ CFM] | AI |  |  | V | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV-SA-F-SP | VAV SUPPLY AIR FLOW SETPOINT |  | RESET SCHED | [0 - ___ CFM] |  |  | C | [ ~ ] | [ ~ ] |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| VAV-D-C | VAV DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | V | [ ~ ] |  | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV-V-C | VAV <REHEAT VALVE> <HEAT ELEMENT> COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | V | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VAV-FAN-SS | VAV FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | V | [ ~ ] |  | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | ZONE TEMPERATURE SETPOINT DEADBAND |  | RESET SCHED | [0 - ___ CFM] |  |  | C | ~ | ~ |  | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| VAV DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [20 empty] | <___>
| VAV VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [20 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [20 empty] | <___>
<___>
OTHER POINTS | VAV-DA-T | VAV DISCHARGE AIR TEMPERATURE | <___> |  | 0-100% OPEN | AO | [~] |  | V | [ ~ ] |  | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  | <___> | <___> | <___> | <___> | <___>
OPTIONAL DCV POINTS | ZN-CO2 | ZONE CO2 | <___> |  | <___> | AI |  |  | V | [V] |  | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> |  |  |  | <___>
| VAV-SA-F-MIN1 | VAV SUPPLY AIR FLOW MINIMUM 1 (DESIGN MINIMUM) |  | [____ CFM] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> |  |  |  | <___>
| VAV-SA-F-MIN2 | VAV SUPPLY AIR FLOW MINIMUM 2 ( SF-ONLY MINIMUM) |  | [____ CFM] |  |  |  | C | VO | [V] |  | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> |  |  |  | <___>
Notes:
|  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  | 3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
|  | 4) | ALARM CONDITIONS MARKED WITH A DOUBLE ASTERISK (**) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN 30 MINUTES.
|  | 5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 14
UNIT HEATER AND CABINET UNIT HEATER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES |  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | OCC/UNOCC | NET-IN |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | <___> |  | OCC/UNOCC | BI |  |  | [ ~ ] | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| EFF-OCC | EFFECTIVE OCCUPANCY | <___> |  | OCC/UNOCC | NET-OUT |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OFF / AUTO | UNIT OFF / AUTO SWITCH | <___> |  | ON/OFF | BI | [~] |  | [ ~ ] | ~ | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE | <___> | [ 82 DEG F ] | <___> | AI |  | C | [ ~ ] | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| HTG-V-C | HEATING VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  | <___> | <___> | <___> | <___>
| HEATING VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
<___>
Notes:
|  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  | 3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
|  | 4) | ALARM CONDITIONS MARKED WITH A DOUBLE ASTERISK (**) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN 30 MINUTES.
|  | 5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
GAS-FIRED INFRARED HEATER
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES |  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | <___> |  | OCC/UNOCC | BI |  |  | [ ~ ] | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| EFF-OCC | EFFECTIVE OCCUPANCY | <___> |  | OCC/UNOCC | NET-OUT |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OFF / AUTO | UNIT OFF / AUTO SWITCH | <___> |  | ON/OFF | BI | [~] |  | [ ~ ] | ~ | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE | <___> | [ 82 DEG F ] | <___> | AI |  | C | [ ~ ] | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| HTG-IR-2P | INFRARED HEATER ON/OFF COMMAND | <___> |  | ON/OFF | BO | [~] |  | VO | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>
PERIMETER RADIATION
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES |  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | OCC/UNOCC | NET-IN |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | <___> |  | OCC/UNOCC | BI |  |  | [ ~ ] | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| EFF-OCC | EFFECTIVE OCCUPANCY | <___> |  | OCC/UNOCC | NET-OUT |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OFF / AUTO | UNIT OFF / AUTO SWITCH | <___> |  | ON/OFF | BI | [~] |  | [ ~ ] | ~ | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE |  | [ 82 DEG F ] | <___> | AI |  | C | [ ~ ] | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-V-C | HEATING VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | V | [ ~ ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HEATING VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
<___>
Notes:
|  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  | 3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
|  | 4) | ALARM CONDITIONS MARKED WITH A DOUBLE ASTERISK (**) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN 30 MINUTES.
|  | 5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
DUAL TEMPERATURE FAN COIL UNIT
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES |  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) |  | <___> | ALM/NORMAL | <BI> | ~ | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | OCC/UNOCC | NET-IN |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | <___> |  | OCC/UNOCC | BI |  |  | [ ~ ] | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| EFF-OCC | EFFECTIVE OCCUPANCY | <___> |  | OCC/UNOCC | NET-OUT |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE TEMPERATURE CONTROL | DTWS-T | DUAL TEMP WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DTWS-T-SP | DUAL TEMP WATER SUPPLY TEMPERATURE SETPOINT |  | <___> | <___> | AI |  | C | V | [ ~ ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-SP-HTG-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE |  | [ 82 DEG F ] | <___> | AI |  | C | [ ~ ] | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-SP-CLG-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE |  | [ 82 DEG F ] | <___> | AI |  | C | [ ~ ] | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-V-C | DUAL TEMP VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OFF / AUTO | UNIT OFF / AUTO SWITCH | <___> |  | ON/OFF | BI | [~] |  | [ ~ ] | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DUAL TEMP VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
<___>
Notes:
|  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  | 3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
|  | 4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
|  | 5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 15
HYDRONIC HEATING HOT WATER FROM DISTRIBUTED STEAM CONVERTER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | HW-PMP-S | HOT WATER PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | SYS-ENA | SYSTEM ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | VO | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HW-PMP-SS | HOT WATER PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | HEATING MODE UNIT STATUS (SEE NOTES) | <___> |  | ON/OFF | NET-OUT |  |  | [V] | ~ | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
HEAT EXCHANGER VALVE CONTROL (STEAM) | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HWS-T | HOT WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | X | HWS-T MORE THAN 41 DEG F ABOVE OR BELOW HWS-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HWS-T-SP | HOT WATER SUPPLY TEMPERATURE SETPOINT |  | [RESET] | <___> |  |  | C | VO | [V] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| STM-V-C | STEAM VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [V] | [X] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| STEAM VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
SYSTEMS SERVED | HTG-RQST1 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_HEAT/ HVAC_OFF | NET-IN |  |  | V | ~ | ~ | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HTG-RQST2 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_HEAT/ HVAC_OFF | NET-IN |  |  | V | ~ | ~ | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | HWR-T | HOT WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 16
HYDRONIC HEATING HOT WATER FROM DISTRIBUTED HTHW CONVERTER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | HW-PMP-S | HOT WATER PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
START/STOP | SYS-ENA | SYSTEM ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | VO | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HW-PMP-SS | HOT WATER PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | HEATING MODE UNIT STATUS (SEE NOTES) | <___> |  | ON/OFF | NET-OUT |  |  | [V] | ~ | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
HEAT EXCHANGER VALVE CONTROL (STEAM) | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HWS-T | HOT WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | X | HWS-T MORE THAN 41 DEG F ABOVE OR BELOW HWS-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HWS-T-SP | HOT WATER SUPPLY TEMPERATURE SETPOINT |  | [RESET] | <___> |  |  | C | VO | [V] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTHW-V-C | HTHW VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [V] | [X] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| HTHW VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
SYSTEMS SERVED | HTG-RQST1 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_HEAT/ HVAC_OFF | NET-IN |  |  | V | ~ | ~ | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| HTG-RQST2 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_HEAT/ HVAC_OFF | NET-IN |  |  | V | ~ | ~ | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  | <___> | <___> | <___> | <___>
OTHER POINTS | HWR-T | HOT WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 17
HYDRONIC HEATING HOT WATER FROM SINGLE BUILDING BOILER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | HW-PMP-S | HOT WATER PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
START/STOP | SYS-ENA | SYSTEM ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | VO | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HW-PMP-SS | HOT WATER PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | HEATING MODE UNIT STATUS (SEE NOTES) | <___> |  | ON/OFF | NET-OUT |  |  | [V] | ~ | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
HEAT EXCHANGER VALVE CONTROL (STEAM) | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HWS-T | HOT WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | X | HWS-T MORE THAN 41 DEG F ABOVE OR BELOW HWS-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HWS-T-SP | HOT WATER SUPPLY TEMPERATURE SETPOINT |  | [RESET] | <___> |  |  | C | VO | [V] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTHW-V-C | HTHW VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [V] | [X] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTHW VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
SYSTEMS SERVED | HTG-RQST1 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_HEAT/ HVAC_OFF | NET-IN |  |  | V | ~ | ~ | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| HTG-RQST2 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_HEAT/ HVAC_OFF | NET-IN |  |  | V | ~ | ~ | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
OTHER POINTS | HWR-T | HOT WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| BLR-S | BOILER STATUS (STATE) | <___> |  | START/STOP | BI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 18
HYDRONIC DUAL-TEMPERATURE SYSTEM WITH STEAM HEAT EXCHANGER AND CHILLED WATER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | HX-P-LL | HEAT EXCHANGER DIFFERENTIAL PRESSURE LOW LIMIT | <___> |  | FLOW/NO FLOW | BI |  |  | V | [ ~ ] | [ ~ ] | * HWS FLOW PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DT-PMP-S | DUAL TEMP PUMP STATUS | <___> |  | ON/OFF |  |  | H | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | SYS-ENA | SYSTEM ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HTG/COOL-MOD | HEATING/COOLING MODE SWITCH | <___> |  | HEAT/COOL | BI |  |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DT-PMP-SS | DUAL TEMP PUMP START/STOP COMMAND | <___> |  | START/STOP | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | HEATING MODE UNIT STATUS (SEE NOTES) | <___> |  | ON/OFF | NET-OUT |  |  | [ V ] | ~ | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
DUAL TEMP SWITCHOVER | DTWR-T | DUAL-TEMP WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DTWR-T-LL | DUAL-TEMP WATER RETURN TEMPERATURE LOW LIMIT |  | 65 DEG F |  |  |  | C | [ ~ ] | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| DTWR-T-HL | DUAL-TEMP WATER RETURN TEMPERATURE HIGH LIMIT |  | 85 DEG F |  |  |  | C | [ ~ ] | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| DT-V-2P | DUAL-TEMP SWITCHOVER VALVE | <___> |  | HEAT/COOL | BO |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-ENA | CHILLER ENABLE | <___> |  | ENABLE/DISABLE | BO |  |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
HEAT EXCHANGER VALVE CONTROL (STEAM) | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HWS-T | HOT WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | HWS-T MORE THAN 41 DEG F ABOVE OR BELOW HWS-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HWS-T-SP | HOT WATER SUPPLY TEMPERATURE SETPOINT |  | [RESET] | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| STM-V-C | STEAM VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| STEAM VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
SYSTEMS SERVED | HTG-RQST1 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_HEAT/ HVAC_OFF | NET-IN |  |  | V | ~ | ~ | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HTG-RQST2 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_HEAT/ HVAC_OFF | NET-IN |  |  | V | ~ | ~ | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | HWR-T | HOT WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DTWS-T | DUAL-TEMP WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 19
HYDRONIC DUAL-TEMPERATURE SYSTEM WITH HIGH TEMPERATURE HOT WATER HEAT EXCHANGER AND CHILLED WATER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[7 empty] | 2 |  |  |  |  | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | HX-P-LL | HEAT EXCHANGER DIFFERENTIAL PRESSURE LOW LIMIT | <___> |  | FLOW/NO FLOW | BI |  |  | V | [ ~ ] | [ ~ ] | * HWS FLOW PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DT-PMP-S | DUAL TEMP PUMP STATUS | <___> |  | ON/OFF |  |  | H | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | SYS-ENA | SYSTEM ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HTG/COOL-MOD | HEATING/COOLING MODE SWITCH | <___> |  | HEAT/COOL | BI |  |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DT-PMP-SS | DUAL TEMP PUMP START/STOP COMMAND | <___> |  | START/STOP | BO | [~] |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | HEATING MODE UNIT STATUS (SEE NOTES) | <___> |  | ON/OFF | NET-OUT |  |  | [ V ] | ~ | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
DUAL TEMP SWITCHOVER | DTWR-T | DUAL-TEMP WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DTWR-T-LL | DUAL-TEMP WATER RETURN TEMPERATURE LOW LIMIT |  | 65 DEG F |  |  |  | C | [ ~ ] | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| DTWR-T-HL | DUAL-TEMP WATER RETURN TEMPERATURE HIGH LIMIT |  | 85 DEG F |  |  |  | C | [ ~ ] | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| DT-V-2P | DUAL-TEMP SWITCHOVER VALVE | <___> |  | HEAT/COOL | BO |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-ENA | CHILLER ENABLE | <___> |  | ENABLE/DISABLE | BO |  |  | VO | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
HEAT EXCHANGER VALVE CONTROL (STEAM) | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HWS-T | HOT WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | HWS-T MORE THAN 41 DEG F ABOVE OR BELOW HWS-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HWS-T-SP | HOT WATER SUPPLY TEMPERATURE SETPOINT |  | [RESET] | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTHW-V-C | HTHW VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| STEAM VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
SYSTEMS SERVED | HTG-RQST1 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_HEAT/ HVAC_OFF | NET-IN |  |  | V | ~ | ~ | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HTG-RQST2 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_HEAT/ HVAC_OFF | NET-IN |  |  | V | ~ | ~ | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | HWR-T | HOT WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DTWS-T | DUAL-TEMP WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 20
HYDRONIC SECONDARY WITH CONSTANT SPEED PUMPING
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
START/STOP | SYS-ENA | SYSTEM ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SEC-PMP-SS | CHILLED WATER PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SEC-PMP-S | CHILLED WATER PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | [ ~ ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 21
SECONDARY HYDRONIC WITH VARIABLE SPEED PUMPING
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
START/STOP | SYS-ENA | SYSTEM ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | V | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SEC-PMP-SS | CHILLED WATER PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | V | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SEC-PMP-S | CHILLED WATER PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
PRESSURE CONTROL | SEC-PMP-C | CHILLED WATER VFD PUMP SPEED COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | V | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SEC-P | CHILLED WATER SUPPLY PRESSURE | <___> |  | <___> | AI |  |  |  | [~] | [~] | * CWS-P MORE THAN 25% ABOVE OR BELOW CWS-P-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SEC-P-SP | CHILLED WATER SUPPLY PRESSURE SETPOINT | <___> | [___] | <___> |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| CHILLED WATER PUMP PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 22
ELECTRIC METER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
REQUIRED POINTS | PWR-TOT | REAL POWER (TOTAL) | <___> |  | 0 - <___> WATTS |  |  |  | V | [~] | X | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KWH-TOT | TOTAL kWh (TOTAL ENERGY) | <___> |  | 0 - <___> kWh |  |  |  | V | [~] | X | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PWR-DEMAND-PEAK | HISTORICAL PEAK DEMAND POWER | <___> |  | 0 - <___> WATTS |  |  |  | V | [~] | X | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PWR-DEMAND | DEMAND POWER | <___> |  | 0 - <___> WATTS |  |  |  | V | [~] | X | [___][~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VOLT-A | RMS VOLTAGE FOR PHASE A | <___> |  | 0 - <___> VOLTS RMS | <AI> |  |  | V | [~] | X | VOLT-A < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VOLT-B | RMS VOLTAGE FOR PHASE B | <___> |  | 0 - <___> VOLTS RMS | <AI> |  |  | V | [~] | X | VOLT-B < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VOLT-C | RMS VOLTAGE FOR PHASE C | <___> |  | 0 - <___> VOLTS RMS | <AI> |  |  | V | [~] | X | VOLT-C < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| AMP-A | RMS CURRENT FOR PHASE A | <___> |  | 0 - <___> AMPS RMS | <AI> |  |  | V | [~] | X | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| AMP-B | RMS CURRENT FOR PHASE B | <___> |  | 0 - <___> AMPS RMS | <AI> |  |  | V | [~] | X | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| AMP-C | RMS CURRENT FOR PHASE C | <___> |  | 0 - <___> AMPS RMS | <AI> |  |  | V | [~] | X | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HZ-AVG | AVERAGE LINE FREQUENCY | <___> |  | 0 - <___> HZ |  |  |  | V | [~] | X | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
OPTIONAL POINTS | PWR-A | REAL POWER FOR PHASE A | <___> |  | 0 - <___> WATTS |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PWR-B | REAL POWER FOR PHASE B | <___> |  | 0 - <___> WATTS |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  | <___> | <___> | <___> | <___>
| PWR-C | REAL POWER FOR PHASE C | <___> |  | 0 - <___> WATTS |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| HZ-A | FREQUENCY FOR PHASE A | <___> |  | 0 - <___> HZ |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| HZ-B | FREQUENCY FOR PHASE B | <___> |  | 0 - <___> HZ |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| HZ-C | FREQUENCY FOR PHASE C | <___> |  | 0 - <___> HZ |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| KVA-TOT | TOTAL kVA | <___> |  | 0 - <___> kVA |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| KVA-A | kVA FOR PHASE A | <___> |  | 0 - <___> kVA |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| KVA-B | kVA FOR PHASE B | <___> |  | 0 - <___> kVA |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KVA-C | kVA FOR PHASE C | <___> |  | 0 - <___> kVA |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KVAR-TOT | TOTAL REACTIVE POWER | <___> |  | 0 - <___> kVA |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KVAR-A | REACTIVE POWER FOR PHASE A | <___> |  | 0 - <___> kVA |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KVAR-B | REACTIVE POWER FOR PHASE B | <___> |  | 0 - <___> kVA |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KVAR-C | REACTIVE POWER FOR PHASE C | <___> |  | 0 - <___> kVA |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KVARH-TOT | TOTAL kVARh (TOTAL REACTIVE ENERGY) | <___> |  | 0 - <___> kVAh |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KVARH-A | kVARh (TOTAL REACTIVE ENERGY) FOR PHASE A | <___> |  | 0 - <___> kVAh |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KVARH-B | kVARh (TOTAL REACTIVE ENERGY) FOR PHASE B | <___> |  | 0 - <___> kVAh |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KVARH-C | kVARh (TOTAL REACTIVE ENERGY) FOR PHASE C | <___> |  | 0 - <___> kVAh |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PF-AVG | AVERAGE POWER FACTOR | <___> |  | -1 TO 1 |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PF-A | POWER FACTOR FOR PHASE A | <___> |  | -1 TO 1 |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PF-B | POWER FACTOR FOR PHASE B | <___> |  | -1 TO 1 |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| PF-C | POWER FACTOR FOR PHASE C | <___> |  | -1 TO 1 |  |  |  | [~] | [~] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 23
GAS METER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
Flow | GAS-F | FLOW RATE | <___> |  | 0 - <___> [CU FT / MIN][CFM] | <PULSE><AI> |  |  | V |  | X | <EXCESSIVE FLOW> | CRIT | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| GAS-F-TOT | TOTAL GAS FLOW | <___> |  | 0 - <___> [CU FT] | <PULSE><AI> |  |  | V | [5 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
|  | FLOW RATE CONFIGURATION |  | <___> | <<___> [CU FT] PER PULSE><___> | <PULSE><AI> |  | C | [19 empty] | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 24
WATER METER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[21 empty] | (THESE COLUMNS AUTO FILL/SHADE) |  |  | (COL AUTO FILL/SHADE | (THESE COLUMNS AUTO FILL/SHADE
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
Flow | WATER-F | WATER FLOW RATE | <___> |  | 0 - <___> [CU FT / MIN][CFM] [GPM] | <PULSE><AI> |  |  | V |  | X | <EXCESSIVE FLOW> | CRIT | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| WATER-F-TOT | TOTAL WATER FLOW | <___> |  | 0 - <___> [CU FT] [GAL] | <PULSE><AI> |  |  | V | [5 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
|  | FLOW RATE CONFIGURATION |  | <___> | <<___> [CU FT] PER PULSE><___> | <PULSE><AI> |  | C | [19 empty] | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 25
SWITCHGEAR
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PRIMARY PLC | PRI-PLC-S | PRIMARY PROGRAMMABLE LOGIC CONTROLLER STATUS | <___> |  | <RUN, STOP, FAULT> | <___> |  |  | V | [~] | [~] | FAULT | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PRI-PLC-V | PRIMARY PROGRAMMABLE LOGIC CONTROLLER POWER SUPPLY VOLTAGE | <___> |  | <___ VOLTS> | AI |  |  | V | [~] | [~] | LOW VOLTAGE | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
SECONDARY PLC | SEC-PLC-S | SECONDARY PROGRAMMABLE LOGIC CONTROLLER STATUS | <___> |  | <RUN, STOP, FAULT> | <___> |  |  | V | [~] | [~] | FAULT | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SEC-PLC-V | SECONDARY PROGRAMMABLE LOGIC CONTROLLER POWER SUPPLY VOLTAGE | <___> |  | <___ VOLTS> | AI |  |  | V | [~] | [~] | LOW VOLTAGE | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
NETWORK PROTECTOR | NET-PROT-S | NETWORK PROTECTOR STATUS | <___> |  | <___> | BI |  |  | V | [~] | [~] | <OPEN> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| NET-PROT-UV | NETWORK PROTECTOR UNDERVOLTAGE | <___> |  | <___> | BI |  |  | V | [~] | [~] | LOW VOLTAGE | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER | ATS-SEL-SWT-P | ATS SELECT SWITCH POSITION | <___> |  | <___> | <___> |  |  | V | [~] | [~] | [___] | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ATS-SRC-SWT-P | ATS SOURCE SWITCH POSITION | <___> |  | <___> | <___> |  |  | V | [~] | [~] | [___] | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ATS-SWT-C | ATS SWITCH COMMAND | <___> |  | <___> | <___> |  |  | V | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
BREAKERS | BKR(1)-S | BREAKER 1 STATUS (OPEN OR CLOSED) | <___> |  | <___> | BI |  |  | V | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| BKR(1)-TRP | BREAKER 1 TRIPPED | <___> |  | <___> | BI |  |  | V | [~] | [~] | TRIPPED | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BKR(2)-S | BREAKER 1 STATUS (OPEN OR CLOSED) | <___> |  | <___> | BI |  |  | V | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| BKR(2)-TRP | BREAKER 1 TRIPPED | <___> |  | <___> | BI |  |  | V | [~] | [~] | TRIPPED | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
<___>
OPTIONAL | RTU-PWR-S | REMOTE TERMINAL UNIT POWER STATUS | <___> |  | <___> | BI |  |  | V | [~] | [~] | [ ~ ] | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SG-CAB-T | SWITCHGEAR CABINET TEMPERATURE | <___> |  | <___> | AI |  |  | V | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | ONLY ONE BREAKER SHOWN. INSERT OTHER BREAKERS

## 26
SUBSTATION
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  |  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  |  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  |  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  |  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
| FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
| VOLTAGE AND CURRENT | VOLT-A | RMS VOLTAGE FOR PHASE A | <___> | ~ | 0 - <___> VOLTS RMS | AI |  |  | V | [V] | [~] | [___] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | VOLT-B | RMS VOLTAGE FOR PHASE B | <___> | ~ | 0 - <___> VOLTS RMS | AI |  |  | V | [V] | [~] | [___] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | VOLT-C | RMS VOLTAGE FOR PHASE C | <___> | ~ | 0 - <___> VOLTS RMS | AI |  |  | V | [V] | [~] | [___] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | FREQ | FREQUENCY | <___> | ~ | 0 - <___> HZ | <___> |  |  | V | [V] | [~] | [___] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | AMP-A | RMS CURRENT FOR PHASE A | <___> | ~ | 0 - <___> AMPS RMS | AI |  |  | V | [V] | [~] | [___] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | AMP-B | RMS CURRENT FOR PHASE B | <___> | ~ | 0 - <___> AMPS RMS | AI |  |  | V | [V] | [~] | [___] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | AMP-C | RMS CURRENT FOR PHASE C | <___> | ~ | 0 - <___> AMPS RMS | AI |  |  | V | [V] | [~] | [___] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| AMBIENT | RH | RELATIVE HUMIDITY | <___> | ~ | 0 - <100> % | AI |  |  | V | [V] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | T | TEMPERATURE | <___> | ~ | <___> | AI |  |  | V | [V] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[16 empty] | <___> | <___> |  | <___>
| OLTC | OLTC-T1 | ON-LOAD TAP CHANGER (OLTC) CONSERVATOR TEMPERATURE | <___> | ~ | <___> | AI |  |  | V | [V] | [~] | [___] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
|  | OLTC-M1 | OLTC CONSERVATOR MOISTURE IN OIL | <___> | ~ | <___> | AI |  | C | V | [V] | [~] | [___] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 27
TRANSFORMER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  |  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  |  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  |  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  |  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
| FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
| ELECTRICAL POINTS | PRIM-VOLT-A | PRIMARY VOLTAGE A | <___> |  | <___> | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | PRIM-VOLT-B | PRIMARY VOLTAGE B | <___> |  | <___> | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | PRIM-VOLT-C | PRIMARY VOLTAGE C | <___> |  | <___> | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | FREQ | FREQUENCY | <___> |  | 0 - <___> HZ | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | PRIM-AMP-A | PRIMARY AMPERAGE A | <___> |  | 0 - <___> AMPS | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | PRIM-AMP-B | PRIMARY AMPERAGE B | <___> |  | 0 - <___> AMPS | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | PRIM-AMP-C | PRIMARY AMPERAGE C | <___> |  | 0 - <___> AMPS | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | SEC-VOLT-A | SECONDARY VOLTAGE A | <___> |  | <___> | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | SEC-VOLT-B | SECONDARY VOLTAGE B | <___> |  | <___> | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | SEC-VOLT-C | SECONDARY VOLTAGE C | <___> |  | <___> | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | SEC-AMP-A | SECONDARY AMPERAGE A | <___> |  | 0 - <___> AMPS | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
|  | SEC-AMP-B | SECONDARY AMPERAGE B | <___> |  | 0 - <___> AMPS | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
|  | SEC-AMP-C | SECONDARY AMPERAGE C | <___> |  | 0 - <___> AMPS | AI |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | KVA | LOAD (KVA) | <___> |  | 0 - 100%, 0 - <___> KVA | NET-OUT |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  | <___> | <___> | <___> | <___>
|  | KW | LOAD (POWER) | <___> |  | 0 - 100%, 0 - <___> KW | NET-OUT |  |  | V | [V] | [~] | < [0.9*NOMINAL] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
| OPTIONAL | OIL-MOIST | OIL MOISTURE | <___> |  | <NORMAL / HIGH> | BI |  |  | V | [V] | [~] | HIGH | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
|  | OA-T | AMBIENT TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [~] | <___> | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
|  | OIL-T | TOP OIL TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [~] | <___> | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
|  | WINDING-T | AVERAGE WINDING TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [~] | <___> | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
Notes:
|  |  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 28
SEWAGE LIFT STATION
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER | CONFIGURATION INFORMATION
PROOFS & SAFETIES | TANK-L | TANK LEVEL | <___> |  | 0 - <___> FEET | BI |  | H | V | [V] | [ ~ ] | <___> | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PP-AMPS-A | PRIMARY PUMP PHASE A AMPS | <___> |  | 0 - <___> AMPS RMS | AI |  |  | V | [V] | [ ~ ] | <___> | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PP-AMPS-B | PRIMARY PUMP PHASE B AMPS | <___> |  | 0 - <___> AMPS RMS | AI |  |  | V | [V] | [ ~ ] | <___> | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PP-AMPS-C | PRIMARY PUMP PHASE C AMPS | <___> |  | 0 - <___> AMPS RMS | AI |  |  | V | [V] | [ ~ ] | <___> | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SP-AMPS-A | SECONDARY PUMP PHASE A AMPS | <___> |  | 0 - <___> AMPS RMS | AI |  |  | V | [V] | [ ~ ] | <___> | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SP-AMPS-B | SECONDARY PUMP PHASE B AMPS | <___> |  | 0 - <___> AMPS RMS | AI |  |  | V | [V] | [ ~ ] | <___> | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SP-AMPS-C | SECONDARY PUMP PHASE C AMPS | <___> |  | 0 - <___> AMPS RMS | AI |  |  | V | [V] | [ ~ ] | <___> | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
START/STOP | PP-SS | PRIMARY PUMP START/STOP COMMAND | <___> |  | ON/OFF | BO | [ ~ ] |  | VO | [VO] | [ ~ ] | PRIMARY PUMP PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SP-SS | SECONDARY PUMP START/STOP COMMAND | <___> |  | ON/OFF | BO | [ ~ ] |  | VO | [VO] | [ ~ ] | SECONDARY PUMP PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
MONITORING | PP-TOT | PRIMARY PUMP RUN TIME | <___> |  |  | NET-OUT |  |  | V | [V] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SP-TOT | SECONDARY PUMP RUN TIME | <___> |  |  | NET-OUT |  |  | V | [V] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| FLOW-R | FLOW RATE | <___> |  |  | <___> |  |  | V | [V] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| FLOW-TOT | TOTALIZED FLOW | <___> |  |  | NET-OUT |  |  | V | [V] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PRECIP | RAINGAUGE PULSE INPUT | <___> |  |  | <___> |  |  | V | [V] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PP-S | PRIMARY PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | [V] | [ ~ ] | PRIMARY PUMP PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SP-S | SECONDARY PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | [V] | [ ~ ] | SECONDARY PUMP PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
CONTROLLER | CONT-BAT-V | CONTROLLER BATTERY BACKUP VOLTAGE | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 29
DOMESTIC HOT WATER BOILER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | HW-PMP-S | HOT WATER PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | [7 empty] | <___>
START/STOP | SYS-ENA | SYSTEM ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | VO | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DHW-PMP-SS | DOMESTIC HOT WATER PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | VO | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | HEATING STATUS | <___> |  | ON/OFF | NET-OUT |  |  | V | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | DHWS-T-SP | DOMESTIC HOT WATER SUPPLY TEMPERATURE SETPOINT |  | [__] | <___> |  |  | C | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DHWR-T | DOMESTIC HOT WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DHW-TANK-T-SP | DOMESTIC HOT WATER TANK TEMPERATURE SETPOINT |  | [__] | <___> |  |  | C | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| DHW-TANK-T | DOMESTIC HOT WATER TANK TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BLR-S | BOILER STATUS (STATE) | <___> |  | START/STOP | BI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 30
HOT WATER BOILER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y | Y | N | N
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y | Y | N | N
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y | N | Y | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | HW-PMP-S | HOT WATER PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | SYS-ENA | SYSTEM ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | VO | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HW-PMP-SS | HOT WATER PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | VO | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | HEATING MODE UNIT STATUS (SEE NOTES) | <___> |  | ON/OFF | NET-OUT |  |  | V | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | HTG-RQST(1) | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | <HVAC_HEAT/ HVAC_OFF><___> | NET-IN |  |  | V | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | MSV <___> | HVAC_STATUS | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HTG-RQST(2) | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | <HVAC_HEAT/ HVAC_OFF><___> | NET-IN |  |  | V | [~] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | MSV <___> | HVAC_STATUS | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | HWS-T-SP | HOT WATER SUPPLY TEMPERATURE SETPOINT |  | [RESET] | <___> | <___> |  | C | VO | [V] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [~] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HWR-T | HOT WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| BLR-S | BOILER STATUS (STATE) | <___> |  | START/STOP | BI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 31
SOLAR HOT WATER
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  |  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  |  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  |  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  |  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
| FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
| HOT WATER GENERATION | SYS-ENA | SYSTEM ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | VO | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | HW-PMP-SS | HOT WATER PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | VO | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | HW-PMP-S | PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | COL-T | COLLECTOR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | CS-T | TEMPERATURE FROM COLLECTOR | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ X ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | CR-T | TEMPERATURE TO COLLECTOR | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | COL-F | FLOWRATE OF COLLECTOR FLUID | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HOT WATER LOAD SIDE | TATOP-T | TEMPERATURE WATER TANK TOP | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | TABOT-T | TEMPERATURE WATER TANK BOTTOM | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | HW-PMP-SS | HOT WATER PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | VO | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | PMP-S | LOAD SIDE PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | DHW-F | FLOWRATE OF DHW | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | HWS-T | HOT WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | HWR-T | HOT WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | [V] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | BTU-HW | BTU METER DHW | <___> |  | <___> | AI |  |  | V | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 32
CHILLED WATER THERMAL STORAGE
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  |  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  |  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  |  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  |  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[13 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
| FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES
| START/STOP | CHLR-1--SS | CHILLER 1 START STOP | <___> |  | START/STOP | BO | [~] |  | VO | [V] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | CHLR-2-SS | CHILLER 2 START STOP | <___> |  | START/STOP | BO | [~] |  | VO | [V] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MODE CONTROLS | V-1 | TANK INLET | <___> | ~ | ON/OFF | BO | [~] |  | VO | [V[O]] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | V-2 | TANK OUTLET | <___> | ~ | ON/OFF | BO | [~] |  | VO | [V[O]] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | V-3 | STAND BY PUMP INLET | <___> | ~ | ON/OFF | BO | [~] |  | VO | [V[O]] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | V-4 | CHILLED WATER RETURN ISOLATION | <___> | ~ | ON/OFF | BO | [~] |  | VO | [V[O]] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | V-5 | CHILLER 1 INLET | <___> | ~ | ON/OFF | BO | [~] |  | VO | [V[O]] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | V-6 | CHILLER 2 INLET | <___> | ~ | ON/OFF | BO | [~] |  | VO | [V[O]] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | PMP-1 | CHILLER 1 INLET PUMP | <___> | ~ | ON/OFF | BO | [~] |  | VO | [V[O]] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | PMP-2 | CHILLER 2 INLET PUMP | <___> | ~ | ON/OFF | BO | [~] |  | VO | [V[O]] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | PMP-3 | STANDBY PUMP 1 | <___> | ~ | ON/OFF | BO | [~] |  | VO | [V[O]] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | PMP-4 | STANDBY PUMP 2 | <___> | ~ | ON/OFF | BO | [~] |  | VO | [V[O]] | [~] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | F-1 | FLOW FROM STORAGE TANK | <___> | ~ | <___> | AI | ~ |  | V | [V] | X | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | F-2 | FLOW METER CHILLED WATER SUPPLY TO BUILDINGS | <___> | ~ | <___> | AI | ~ |  | V | [V] | X | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | F-3 | BYPASS FLOW METER | <___> | ~ | <___> | AI | ~ |  | V | [V] | X | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | P-1 | DIFFEREENTIAL PRESSURE CHILLED WATER | <___> | ~ | <___> | AI | ~ |  | V | [V] | X | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
|  | THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 33
Water Cooled Centrifugal Chiller Interface
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | CHLR-S | CHILLER STATUS | <___> |  | ON/OFF | BI |  |  | V | V | X | CHILLER STATUS NOT EQUAL TO COMMAND | [info] [crit] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | [~] | [___] | [___] | [___]
| CHLR-ENA | CHILLER ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | VO | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-SS | CHILLER START-STOP (ON/OFF) COMMAND | <___> |  | [___] | BO | [~] |  | VO | V | [ ~ ]
| CHLR-MOD | CHILLER MODE | <___> |  | ON/OFF | NET-IN |  |  | V | V | [ ~ ]
| CHLR-ALM | CHILLER ALARM DESCRIPTION | <___> |  | [ALM/NORMAL] | NET-IN |  |  | V | V
COMPRESSOR | KVA-COMP | COMPRESSOR POWER | <___> |  | 0 - <___> KW | NET-IN |  |  | V | V |  |  |  |  | MSV <___> |  |  | <___> | <___> | <___>
| COMP(1)-S | COMPRESSOR 1 RUN STATUS | <___> |  | ON/OFF | BI |  |  | V |  | X |  | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| COMP(2)-S | COMPRESSOR 2 RUN STATUS | <___> |  | ON/OFF | BI |  |  | V |  | X
| COMP-OIL-T | COMPRESSOR OIL TEMPERATURE | <___> |  | [ DEG F] | BO |  |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___>
| HIGH-OIL-P | HIGH SIDE COMPRESSOR OIL PRESSURE | <___> |  | [ PSI] | AI
| LOW-OIL-P | LOW SIDE COMPRESSOR OIL PRESSURE | <___> |  | [ PSI] | AI
EVAPORATOR | EVAP-P-1 | EVAPORATOR PRESSURE COMPRESSOR 1 | <___> |  | [ PSI] | AI |  |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| EVAP-P-2 | EVAPORATOR PRESSURE COMPRESSOR 2 | <___> |  | [ PSI] | AI |  |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
| EVAP-F | EVAPORATOR WATER FLOW RATE | <___> |  | [ GPM] | AI |  |  | V | V | X
| EVAP-IN-T | EVAPORATOR INLET TEMPERATURE | <___> |  | <___> | AI |  |  | V | V | X
| EVAP-OUT-T | EVAPORATOR OUTLET TEMPERATURE | <___> |  | <___> | AI |  |  | V | V | X |  |  |  | <___> |  |  | <___> | <___> | <___>
| EVAP-PMP-SS | EVAPORATOR PUMP START REQUEST | <___> |  | ON/OFF | BO |  |  |  |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| EVAP-PMP-S | EVAPORATOR PUMP STATUS (FLOW PROOF) | <___> |  | ON/OFF | BI |  |  | V | V |  | EVAP PUMP PROOF FAILED | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| EVAP-REF-T | EVAPORATOR REFRIGERANT TEMPERATURE | <___> |  | <___> | AI |  |  | V | V | X | [ ~ ] |  | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| EVAP-REF-P | EVAPORATOR REFRIGERANT PRESSURE | <___> |  | [ PSI] | AI |  |  | V |  | X | <___> | [info] [crit] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
CONDENSOR | COND1-P | CONDENSOR 1 PRESSURE | <___> |  | [ PSI] | AI |  |  | VO |  | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COND-IN-T | CONDENSOR INLET TEMPERATURE | <___> |  | [ DEG F] | AI |  |  | V |  | X
| COND2-P | CONDENSOR 2 PRESSURE | <___> |  | [ PSI] | AI |  |  |  |  | X |  |  |  | <___> |  |  | <___> | <___> | <___> | [7 empty] | <___>
| COND-OUT-T | CONDENSOR OUTLET TEMPERATURE | <___> |  | [ DEG F] | AI |  |  | V | V | X |  |  |  | <___> |  |  | <___> | <___> | <___>
| COND-PMP-SS | CONDENSOR PUMP START REQUEST | <___> |  | ON/OFF | BO |  |  |  |  | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| COND-PMP-S | CONDENSOR PUMP STATUS (FLOW PROOF) | <___> |  | ON/OFF | BI |  |  | V | V |  | EVAP PUMP PROOF FAILED | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| COND-REF-T | CONDENSOR REFRIGERANT TEMPERATURE | <___> |  | [ DEG F] | AI |  |  | V | V | X | [ ~ ] |  | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| COND-REF-P | CONDENSOR REFRIGERANT PRESSURE | <___> |  | [ PSI] | AI |  |  | V | V | X | <___> | [info] [crit] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
ELECTRICAL | VOLT-A | RMS VOLTAGE FOR PHASE A | <___> |  | 0 - <___> VOLTS RMS | <AI> |  |  | V |  | X |  |  |  | <___> |  | SNVT_volts_f | <___> | <___> | <___> |  |  |  | <___> | <___> | <___> | <___>
| VOLT-B | RMS VOLTAGE FOR PHASE B | <___> |  | 0 - <___> VOLTS RMS | <AI> |  |  | V |  | X |  |  |  | <___> |  | SNVT_volts_f | <___> | <___> | <___> |  |  |  | <___> | <___> | <___> | <___>
| VOLT-C | RMS VOLTAGE FOR PHASE C | <___> |  | 0 - <___> VOLTS RMS | <AI> |  |  | V |  | X |  |  |  | <___> |  | SNVT_volts_f | <___> | <___> | <___> |  |  |  | <___> | <___> | <___> | <___>
| AMP-A | RMS CURRENT FOR PHASE A | <___> |  | 0 - <___> AMPS RMS | <AI> |  |  | V |  | X |  |  |  | <___> |  | SNVT_amp_f | <___> | <___> | <___> |  |  |  | <___>
| AMP-B | RMS CURRENT FOR PHASE B | <___> |  | 0 - <___> AMPS RMS | <AI> |  |  | V |  | X |  |  |  | <___> |  | SNVT_amp_f | <___> | <___> | <___> |  |  |  | <___>
| AMP-C | RMS CURRENT FOR PHASE C | <___> |  | 0 - <___> AMPS RMS | <AI> |  |  | V |  | X |  |  |  | <___> |  | SNVT_amp_f | <___> | <___> | <___> |  |  |  | <___>
SYSTEM | LVG-WATER-T | CHILLED WATER SUPPLY TEMP | <___> |  | [ DEG F] | AI |  |  | V | V | X | [ ~ ] |  | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| RET-WATER-T | CHILLED WATER RETURN TEMPERATURE | <___> |  | [ DEG F] | AO |  |  | V | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ENT-COND-T | ENTERING CONDENSOR WATER TEMPERATURE | <___> |  | [ DEG F] | AI |  |  | V | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
| EXT-COND-T | EXITING CONDENSOR WATER TEMPERATURE | <___> |  | [ DEG F] | AI |  |  | V | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
| CWS-T-SP | CHILLED WATER SUPPLY TEMP SETPOINT |  | [___ DEG F] | [ DEG F] | [___] |  | C | VO | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CWS-ACT-T-SP | CHILLED WATER ACTIVE TEMP SETPOINT |  | [___ DEG F] | [ DEG F] |  |  | C | VO | V
| COND-F | CONDENSOR WATER FLOW RATE | <___> |  | [ GPM] | AI |  |  | V | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-CAP-LIM | MAXIMUM CAPACITY LEVEL |  | [___] | <___> | BO |  |  | VO | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-HTG-T-SP | CHILLER SETPOINT WHEN IN HEATING MODE |  | [___ DEG F] | [ DEG F] |  |  | C | [6 empty] | <___> |  |  | <___> | <___> | <___> | [7 empty] | <___>
| CHLR-CAP | OPERATING CAPACITY | <___> |  | [ TONS]
| CHLR-CAP-LIM | CURRENT CAPACITY LMIT |  | [___] | [ TONS]
OTHER POINTS | OILHIA-P | HIGH SIDE OIL PRESSURE ABSOLUTE | <___> |  | [ PSI] | AI |  |  | V |  |  | [ ~ ] |  | [ ~ ] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| OILHID-P | HIGH SIDE OIL PRESSURE DIFFERENTIAL | <___> |  | [ PSI] | AI |  |  | V
| OILLOWA-P | LOW SIDE OIL PRESSURE ABSOLUTE | <___> |  | [ PSI] | AI |  |  | V
| OILLOWD-P | LOW SIDE OIL PRESSURE DIFFERENTIAL | <___> |  | [ PSI] | AI |  |  | V
| OILA-T | OIL TEMPERATURE ABSOLUTE | <___> |  | [ DEG F] | AI |  |  | V |  |  | [ ~ ] |  | [ ~ ]
| OILD-T | OIL TEMPERATURE DIFFERENTIAL | <___> |  | [ DEG F] | AI |  |  | V
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>
|  |  | 7) | CONTRACTOR SHALL LIST ALL CHILLER ALARMS AVAILABLE TO THE NETWORK

## 34
Air Cooled Centrifugal Chiller Interface
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFTIES | CHLR-S | CHILLER STATUS | <___> |  | ON/OFF | BI |  |  | V | V |  | CHILLER STATUS NOT EQUAL TO COMMAND | [info] [crit] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | [~] | [___] | [___] | [___]
| CHLR-SS | CHILLER START-STOP (ON/OFF) COMMAND | <___> |  | ON/OFF | BO | [~] |  | V | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-MOD | CHILLER MODE - OPERATIONAL CODE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | V | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-ALM | CHILLER ALARM/FAULT | <___> |  | ALM/NORMAL | BI |  | H |  |  |  | ALM | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| CHLR-LOW-T | CHILLER LOW TEMP CUTOUT | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H |  |  |  | ALM | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| CHLR-LO | SYSTEM 1 LOCKOUT | <___> |  | ON/OFF | NET-IN |  |  | V | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
COMPRESSOR | COMP1-S | COMPRESSOR 1 RUN STATUS | <___> |  | ON/OFF | BI |  |  | V | V | X | COMPRESSOR PUMP PROOF FAILED | [info] [crit] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | [~] | [___] | [___] | [___]
| COMP2-S | COMPRESSOR 2 RUN STATUS | <___> |  | ON/OFF | BI |  |  | V | V | X | COMPRESSOR PUMP PROOF FAILED | [info] [crit] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | [~] | [___] | [___] | [___]
EVAPORATOR | EVAP-PMP-S | EVAPORATOR PUMP STATUS (FLOW PROOF) | <___> |  | ON/OFF | BI |  |  | V | V |  | EVAP PUMP PROOF FAILED | [info] [crit] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | [~] | [___] | [___] | [___]
CONDENSOR | COND-FANS-S | CONDENSER FAN STATUS | <___> |  | ON/OFF | NET-IN |  |  | V | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___>
SYSTEM | LVG-WATER-T | CHILLED WATER TEMP LEAVING CHILLER | <___> |  | [ DEG F] | AI |  |  | V | V |  | [ ~ ] |  | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| RET-WATER-T | RETURN CHILLED WATER TEMPERATURE | <___> |  | [ DEG F] | AI |  |  | V | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CONTMODE | CONTROL MODE - LOCAL OR REMOTE | <___> |  | LOCAL/REMOTE | NET-IN |  |  | V | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CWS-T-SP | CHILLED WATER SUPPLY TEMP SETPOINT | <___> | [___DEG F] | [ DEG F] | AO |  |  | VO | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-RUN-H | CHILLER RUNTIME HOURS | <___> |  |  | AI |  |  | V | V
OTHER POINTS | CHLR-CL | CURRENT LIMIT | <___> | [___ AMP] | [ AMP]
| CHLR-SUC-T | SUCTION TEMPERATURE | <___> |  | [ DEG F] | AI |  |  | V | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-DIS-T | DISCHARGE TEMPERATURE | <___> |  | [ DEG F] | AI |  |  | V | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-OIL-T | OIL TEMPERATURE | <___> |  | [ DEG F] | AI |  |  | V | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-OIL-P | OIL PRESSURE | <___> |  | [ PSI] | AI |  |  | V |  | X | <___> | [info] [crit] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
| CHLR-SUC-P | SUCTION PRESSURE | <___> |  | [ PSI] | AI |  |  | V |  | X | <___> | [info] [crit] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
| CHLR-DIS-P | DISCHARGE PRESSURE | <___> |  | [ PSI] | AI |  |  | V |  | X | <___> | [info] [crit] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
| CHLR-FL-AMP | FULL LOAD AMP | <___> |  | 0 - <___> kVA |  |  |  | [~] |  | X |  |  |  | <___> |  | SNVT_power_f | <___> | <___> | <___> |  |  |  | <___>
| CHLR-SUCSH-T | SUCTION SUPERHEAT TEMPERATURE | <___> |  | [ DEG F] | AI |  |  | V | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CHLR-DISSH-T | DISCHARGE SUPERHEAT TEMPERATURE | <___> |  | [ DEG F] | AI |  |  | V | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OA-T | OUTSIDE AIR AMBIENT TEMPERATURE | <___> | [___DEG F] | [ DEG F] | AI |  |  | V | V
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <_____>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <_____>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <_____>

## 35
GENERATOR
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
COLUMN IS USED FOR BACNET (NO NIAGARA)
COLUMN IS USED FOR BACNET (WITH NIAGARA)
COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA)
COLUMN IS USED FOR LONWORKS (WITH NIAGARA)
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS AND SAFETIES | FAULT | GENERATOR FAULT STATUS | <___> | ~ | ALM/NORMAL | <___> |  |  | V | V | [___] | FAULT | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| FAULT-RST | GENERATOR FAULT RESET | <___> | ~ | <___> | <___> |  |  | VO | VO | [___] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
START/STOP | GEN-SS | GENERATOR START/STOP | <___> | ~ | ON/OFF | <___> |  |  | VO | [V[O]] | [~] | <FAILURE TO START> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| GEN-S | GENERATOR ENGINE STATUS | <___> | ~ | ON/OFF | <___> |  |  | V | [V] | [~] | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ELECTRICAL/GENERATOR POINTS | KW | GENERATOR LOAD (KW) - REAL POWER | <___> | ~ | 0 - <___> KW | <___> |  |  | V | [V] | X | <NEAR CAPACITY> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KVA | GENERATOR LOAD (Power) - APPARENT POWER | <___> | ~ | 0 - 100%, 0 - <___> KVA | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KVAR | GENERATOR LOAD (KVAR) - REACTIVE POWER | <___> | ~ | 0 - <___> KVAR | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VOLT-A | RMS VOLTAGE FOR PHASE A | <___> | ~ | 0 - <___> VOLTS RMS | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VOLT-B | RMS VOLTAGE FOR PHASE B | <___> | ~ | 0 - <___> VOLTS RMS | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VOLT-C | RMS VOLTAGE FOR PHASE C | <___> | ~ | 0 - <___> VOLTS RMS | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VOLT-AB | VOLT-AB | <___> | ~ | 0 - <___> VOLTS RMS | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VOLT-BC | VOLT-BC | <___> | ~ | 0 - <___> VOLTS RMS | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| VOLT-CA | VOLT-CA | <___> | ~ | 0 - <___> VOLTS RMS | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| FREQ | FREQUENCY | <___> | ~ | 0 - <___> HZ | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| AMP-A | RMS CURRENT FOR PHASE A | <___> | ~ | 0 - <___> AMPS | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| AMP-B | RMS CURRENT FOR PHASE B | <___> | ~ | 0 - <___> AMPS | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| AMP-C | RMS CURRENT FOR PHASE C | <___> | ~ | 0 - <___> AMPS | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| KWH | KILOWATT HOURS | <___> | ~ | 0 - <___> KWH | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| PF | POWER FACTOR | <___> | ~ | <___> | <___> |  |  | V | [V] | X | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ENGINE | [HIGH-EXH-TMP] | GENERATOR HIGH EXHAUST TEMPERATURE | <___> | ~ | <___> | <___> |  |  | V | [V] | [~] | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| [HIGH-VIB] | GENERATOR HIGH VIBRATION | <___> | ~ | <___> | <___> |  |  | V | [V] | [~] | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RPM | RPM | <___> | ~ | <___> | <___> |  |  | V | [V] | [~] | RPM > [Maximum Allowed] | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OIL-PRES | OIL PRESSURE | <___> | ~ | <___> | <___> |  |  | V | [V] | [~] | ALM | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| [OIL-T] | OIL TEMPERATURE | <___> | ~ | <___> | <___> |  |  | V | [V] | [~] | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| [COOL-L] | COOLANT LEVEL | <___> | ~ | <___> | <___> |  |  | V | [V] | [~] | LOW | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOL-T | COOLANT TEMP | <___> | ~ | <___> | <___> |  |  | V | [V] | [~] | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RUN-H | ENGINE RUNNING HOURS | <___> | ~ | <___> | <___> |  |  | V | [V] | [~] | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
FUEL | FUEL-Q | FUEL QUANTITY | <___> | ~ | <___> | <___> |  |  | V | [V] | [~] | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| FUEL-L | GENERATOR FUEL LEVEL OR QUANTITY | <___> | ~ | <___> | <___> |  |  | V | [V] | [~] | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| [PMP-FLT] | GENERATOR FUEL PUMP FAULT | <___> | ~ |  | <___> |  |  | V | [V] | [~] | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
<___>
OTHER | BAT-CV | BATTERY OR CHARGING VOLTAGE | <___> | ~ | <___> | <___> |  |  | V | [V] | [~] | <___> | [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>
|  |  | 7) | ONLY ONE BREARKER SHOWN. INSERT OTHER BREAKERS

## 36
DEDICATED OUTSIDE AIR UNIT
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | V |  | SUPPLY FAN PROOF FAILED | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| EF-S | EXHAUST FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | V |  | EXHAUST FAN PROOF FAILED | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H |  |  |  | ALM | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| EA-SMK | EXHAUST AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | [6 empty] | <___> |  |  | <___> | <___> | <___>
| HTG-DA-T-LL | HEATING COIL DISCHARGE TEMPERATURE LOW LIMIT SWITCH | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H |  |  |  | ALM | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) |  |  |  | BI |  | H | [6 empty] | <___> | <___> | <___> | <___> | <___> | <___>
| OA-FLT-P-HL | AIR FILTER PRESSURE HIGH LIMIT SWITCH |  | <___> | ALM/NORMAL | BI |  | H | V |  |  | [ALM] | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | V |  |  |  |  | MSV <___> |  |  | <___> | <___> | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| EF-SS | EXHAUST FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| UNIT STATUS | UNIT STATUS (SEE NOTE) | <___> |  | ON/OFF | NET-OUT |  |  | V | [5 empty] | <___> | <___> | HVAC_STATUS | <___> | <___> | <___>
FAN CAPACITY CONTROL | SA-F | SUPPLY AIR FLOW | <___> |  | <___> | AI |  |  |  |  | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
| EA-F | EXHAUST AIR FLOW | <___> |  | <___> | AI |  |  |  |  | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
SUPPLY AIR TEMPERATURE | SA-T | SUPPLY AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V |  | X | *SA-T MORE THAN 10 DEG F ABOVE OR BELOW SETPOINT | [info] [crit] | [___] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
| SA-T-SP | SUPPLY AIR TEMPERATURE SETPOINT |  | [55 DEG F] | <___> |  |  | C | VO | VO |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
| CLG-V-C | COOLING VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | COOLING VALVE PID LOOP SETTINGS |  | <___> |  |  |  | C | [6 empty] | <___> |  |  | <___> | <___> | <___> | [7 empty] | <___>
| HTG-V-C | HEATING VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
|  | HEATING VALVE PID LOOP SETTINGS |  | <___> |  |  |  | C | [6 empty] | <___> |  |  | <___> | <___> | <___> | [7 empty] | <___>
OTHER POINTS | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V |  |  | [ ~ ] |  | [ ~ ] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| EA-T | EXHAUST AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V |  |  | [ ~ ] |  | [ ~ ] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
ENERGY RECOVERY VENTILATOR (ERV) POINTS | OA2-T | OUTSIDE AIR TEMPERATURE 2 (DISCHARGE OF HEAT WHEEL) | <___> |  | <___> | AI |  |  | V |  |  | [ ~ ] |  | [ ~ ] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| EA2-T | EXHAUST AIR TEMPERATURE 2 (DISCHARGE OF HEAT WHEEL) | <___> |  | <___> | AI |  |  | V |  |  | [ ~ ] |  | [ ~ ] | <___> | <___> | TEMP_P | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| ERV-S | ENERGY RECOVERY VENTILATOR FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | V |  | ERV FAN PROOF FAILED | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| ERV-SS | ENERGY RECOVERY VENTILATOR FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ERV-FLT-P-HL | ERV AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V |  |  | [ALM] | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <_____>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <_____>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <_____>

## 37
CHILLED WATER PLANT (PRIMARY / SECONDARY SYSTEM, IN CONJUNCTION WITH AIR AND/OR WATER COOLED CHILLER))
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | CHW-PRIM-PMP-S | CHILLED WATER PRIMARY PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | V |  | PRIAMARY PUMP PROOF FAILED | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| CHW-SEC-PMP-S | CHILLED WATER SECONDARY PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | V |  | SECONDARY PUMP PROOF FAILED | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| CW-PMP-S | CONDENSER WATER PUMP STATUS | <___> |  | ON/OFF | BI |  |  | V | V |  | CONDENSER PUMP PROOF FAILED | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| CT-S | COOLING TOWER FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | V |  | COOLING TOWER PROOF FAILED | [info] [crit] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
START/STOP | SYS-ENA | SYSTEM ENABLE | <___> |  | ENABLE/DISABLE | NET-IN |  |  | VO | [5 empty] | BV <___> |  |  | <___> | <___> | <___> | <___> | <___> | <___>
| ChW-PRIM-PMP-SS | CHILLED WATER PRIMARY PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ChW-SEC-PMP-SS | CHILLED WATER SECONDARY PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CW-PMP-SS | CONDENSER WATER PUMP START/STOP | <___> |  | START/STOP | BO | [~] |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CT-SS | COOLING TOWER FAN START/STOP | <___> |  | START/STOP | BO | [~] |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CT-C | COOLING TOWER COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | V |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING TOWER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| UNIT STATUS | CHILLER UNIT STATUS (SEE NOTES) | <___> |  | ON/OFF | NET-OUT |  |  | V | [5 empty] | <___> |  |  | <___> | <___> | <___>
TEMPERATURE CONTROL | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | V | X | [ ~ ] | [ ~ ] | [___] | <___> |  |  | <___> | <___> | <___> |  |  |  |  | [___] | [___] | [___]
| ChWS-T | CHILLED WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | V | X | ChWS-T MORE THAN 5 DEG F ABOVE OR BELOW CHWS-T-SP, AFTER THE SYSTEM HAS BEEN ENABLED FOR 30 MINUTES | [info] [crit] | [ ~ ] | <___> |  |  | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
| ChWS-T-SP | CHILLED WATER SUPPLY TEMPERATURE SETPOINT |  | [RESET] | <___> |  |  | C | VO | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
FLOW CONTROL | ChW-SEC-PMP-C | CHILLED WATER SECONDARY PUMP COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ChW-SEC-P | CHILLED WATER SECONDARY PUMP LOOP PRESSURE | <___> |  | <___> | AI |  |  |  |  | X | *MORE THAN 20% ABOVE OR BELOW SETPOINT | [info] [crit] | [___] | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
| ChW-SEC-P-SP | CHILLED WATER SECONDARY PUMP LOOP PRESSURE SETPOINT |  | [ RESET ] | <___> |  |  | C | VO | V | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
|  | SUPPLY PUMP PID LOOP SETTINGS |  | <___> |  |  |  | C | [6 empty] | <___> |  |  | <___> | <___> | <___> | [7 empty] | <___>
SYSTEMS SERVED | CLG-RQST1 | CLG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_COOL/ HVAC_OFF | NET-IN |  |  | V |  | X |  |  |  | BV <___> |  | HVAC_STATUS | <___> | <___> | <___>
| CLG-RQST2 | CLG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | <___> |  | HVAC_COOL/ HVAC_OFF | NET-IN |  |  | V |  | X |  |  |  | BV <___> |  | HVAC_STATUS | <___> | <___> | <___>
OTHER POINTS | ChWR-T | CHILLED WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | V | X |  |  |  | <___> |  |  | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
| CWS-T | CONDENSER WATER SUPPLY TEMPERATURE | <___> |  | <___> | AI |  |  | V | V | X |  |  |  | <___> |  |  | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
| CWR-T | CONDENSER WATER RETURN TEMPERATURE | <___> |  | <___> | AI |  |  | V | V | X |  |  |  | <___> |  |  | <___> | <___> | <___> |  |  |  | <___> | [___] | [___] | [___]
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A COOLING/COOLING REQUEST TO THE BOILER, COOL EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC ChW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <_____>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC ChW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <_____>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC ChW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <_____>
|  |  | 7) | FOR LEAD/LAG PUMPS, FANS, OR CHILLERS, INSERT ADDITIONAL ROWS TO REPRESENT ALL DEVICES (E.G., CW-PMP1-S, CW-PMP2-S, ETC)
|  |  | 8) | ASSUMES VARIABLE SPEED ON SECONDARY FLOW ONLY, FOR VARIABLE SPEED PRIMARY, CONDENSER, OR COOLING TOWER LOOPS ADD COMMAND POINTS (E.G., ChW-SEC-PMP-C)