## Introduction - READ FIRST
Site Name:
Designer:
Date Sent:
Date Due Back:
This spreadsheet provides guidance regarding coordination requirements for the execution of Cybersecurity design according to UFC 4-010-06, Cybersecurity of Facility Control Systems, and UFGS 25 05 11, Cybersecurity for Facility Control Systems.
Both design processes, following the UFC and development of a specification, require numerous coordination steps with others. Unfortunately, while the coordination requirements can be reasonably well defined, the personnel that need to be coordinated with varies widely, both among the services and also from project site to project site.
This sheet is intended for use by the Cybersecurity designer, but requires customization prior to its use. The sheet has bracketed options (similar to what appears in a guide specification) to allow selection of specific answers to topics. The project manager or (for contracted projects) the COTR should select options before forwarding this sheet to the Cybersecurity designer.
This sheet has three tabs
| 1) | The first tab (POC) describes personnel, both design and site, associated with the project and then provides a decision tree to help the designer determine who to coordinate with. This is organized as a group of topics related to the design; for each topic there is a series of questions to lead the designer to the correct person to coordinate with on that specific topic.
Note that the answer to these questions greatly depend on the designer's organization -- a private A&E may have all questions answered by a single government POC (who forwards issues to other goverement personnel) while a government designer working at an installation may have direct access to personnel with "ultimate" decision authority.
| 2) | A tab (UFC) describing the main coordination decisions required to execute the UFC. These are mainly determination of the CIA rating and possible adjustments to that rating and use of UFGS 25 05 11 or independent development of a cybersecurity specification
| 3) | A tab (UFGS) going through UFGS 25 05 11 and covering coordination issues in the development of a project-specific specification based on that UFGS. Many of these coordination issues directly relate to designer options within the specification, while others are more "what if" issues such as submittal reviewers and broad system issues such as use of wireless.

## POC
This sheet will attempt to help define contacts for coordination issues. It defines roles, then provides guidance on which role to coordinate with for specific issues.
Definition of roles/pesonnel
Role |  |  |  | Defintion |  | Name, Contact information
System Owner |  |  | SO | The person directly responsible for the system. For most (if not all) FRCS, this will be a facilities person. For some FRCS supporting critical missions, it is possible that the SO will be a representative from the tenant mission organization. In many cases, it will be difficult to identify this person as often no individual has sufficient authority and focus to realistically be considered the system owner.
Authorizing Offical |  |  | AO | A person who has the ultimate authority to approve operation of the system. Each service has a fairly short list of AOs, and determination of the AO is not difficult. However, the AO is almost never the "correct" contact for the issue, and they are included here largely for completeness.
Controls Designer |  |  | CD | The designer of the FRCS. Generally, but not always, the same as the person executing UFC 4-010-06 and developing a project-specific specification.
Controlled Equipment Designer |  |  | CE | The designer of the equipment controlled by the FRCS. For example, for an HVAC control system, the controlled equipment is the air handler, ductwork, coils, piping, pumps, fans, etc. and the controlled equipment designer is the mechanical engineer.
Physical Security Designer |  |  | PS | The designer reponsible for physical security in the space occupied by the FRCS, the controlled equipment, and potentially the tenant supported by the FRCS.
Building O&M contact |  |  | O&M | A person who will have responsbility for day-to-day operations and maintenance of the FRCS and the controlled equipment. This is likely a facilities person, but for critical installations might be a mission tenant person.
Site IT contact |  |  | IT | A general site person capable of addressing basewide IT issues.
Information System Security Officer |  |  | ISSO | A technical person for cybersecurity questions directly related to the FRCS. This person may not yet exist at this phase of the project.
Contracting Officer |  |  | KO | Government offical capable of approving contractual changes.
Contracting Officer Representative |  |  | COR | For a private A&E designer, this may be the primary contact for project coordination.
Fire Marshall |  |  | FM | Questions about Fire Protection systems may need to coordinate with the site Fire Marshall
Project Manager |  |  | PM | General person responsible for the overall execution of the design phase of the project.
Prior to forwarding this to the designer (private contractor or government), provide the proper POCs in the table below.
The following table presents topics and a list of people to coordinate with.
If your topic is: |  |  |  | Who likely has the information: | If you are a private contractor, talk to: | If your are govt, talk to:
Controlled equipment design |  |  |  | Your controlled equipment designer | Your controlled equipment designer | Your controlled equipment designer
Physical Security |  |  |  | Your Physical Security designer | Your Physical Security designer | Your Physical Security designer
Any issue requiring coordination with the govt. |  |  |  | COR | Your govt. contact | [Your project PM][___]
| Any issue that might impact your contract |  |  | COR or KO | [KO][___]
| General |  |  | SO, IT | [COR][___] | [PM][___]
| Passwords |  |  | O&M | [COR][___] | [PM][___]
| General FRCS cyber functionality |  |  | SO, ISSO | [COR][___] | [PM][___]
| Wireless |  |  | SO, IT | [COR][___] | [PM][___]
| Site IT support issues |  |  | IT | [COR][___] | [PM][___]
|  | HTTPS certificates |  | IT | [COR][___] | [PM][___]
|  | email access |  | IT | [COR][___] | [PM][___]
|  | Mobile code |  | IT | [COR][___] | [PM][___]
|  | PKI |  | IT | [COR][___] | [PM][___]
|  | Use of govt. computers |  | IT | [COR][___] | [PM][___]

## UFC
UFC Process Checklist |  |  | Answers
Determine CIA Rating
Is the CIA Rating Given? Coordinate with the SO to get this rating.
NO | Use Appendix F of UFC to compute the CIA rating. Document the rating and the assumptions made.
Is the CIA rating LOW?
NO | A MODERATE or HIGH control system requires a MODERATE or HIGH controlled system -- the underlying equipment (typically electrical or mechanical) must be designed to a MODERATE or HIGH impact level. Some suggestions for what this requires are mentioned in Appendix F of the UFC. Coordinate with other design diciplines (primarily electrical and mechanical) to confirm that they have implemented system design elements consistent with a electrical and mechanical equipment rating above LOW. If not, reevaluate the assigned CIA rating.
NO | Consider the potential to lower the CIA rating by using one or more of the techniques in section 3-2.2 of the UFC. This may add more cost on the equipment side, but particularly if connection to a LOW basewide system is desired, it may be the cost effective approach.
Determine applicabilty of UFGS 25 05 11
DOD 8500 provides references with lists of CCIs to implement as a basis of a cybersecurity specification. UFGS 25 05 11 is the recommended alternative to this approach but does not always require all the CCIs recommended by DODI 8500. Unless there is strong opposition from the SO or AO, assume that UFGS 25 05 11 will be used to develop a project specification. Note that the project specification must support the DoD construction process, which does not necessarily have the same requirements or goals as the DoD RMF process.
YES, use UFGS 25 05 11 | Use UFGS 25 05 11
Can the requirements of 25 05 11 be readily met?
| NO | What are potential hurdles and are there other control system options (perhaps at a higher price) that might meet the requirements?
If the impact rating is MODERATE, can section 3-2.2 of the UFC be used to lower the rating to LOW?
Are there additional compensating requirements? Typcially, physical security, manual controls, and equipment redundancy can be used to reduce the impact of the controls.
Discuss the situation with the SO and see if they are willing to either accept a less-secure system or are willing to provide more funding.
NO, don't use UFGS 25 05 11 | Use Sections 3-3 to 3-6 of UFC to make a project specification
The UFC describes the following 4-step (2A, 2B, 2C, and 3) process. It also provides a number of tables of CCIs which (as described below) assisst the designer.
| Step2A | Use the impact level to select controls from NIST SP 800-82
| Step 2B | Use DoD master CCI list to develop a list of relevant CCIs based on the controls selected in step 2A
| Step 2C | Categorize CCIs and identify CCIs that require input from the designer or are the designer responsibility
| Step 3 | Develop a specification which includes cybersecurity requirements, and provide input to others as needed.
The following tables were created to assist the designer by pairing down anticipated DESIGNER controls.
| i. | TABLE H-4 lists all the recommended DESIGNER responsibility controls for LOW systems.
| ii. | TABLE H-5 lists the recommended DESIGNER responsibility controls for MODERATE systems.
| iii. | Therefore, if a system is deemed MODERATE, the DESIGNER would address the controls in TABLE H-4 and TABLE H-5.
| iv. | TABLE H-6 and TABLE H-7 respectively lists the recommended PLATFORM ENCLAVE controls for LOW and MODERATE. In essence, these are the control that the DESIGNER could list as to be expected to be INHERITED if the system is on a network not solely maintained by the ISO.

## UFGS
UFGS Process Checklist
Item | UFGS Section | Section Title | Who | Issue to be addressed | Effect on Contract Package | Final Decision | Done/Date
1 | 1 | General | COTR/PM | Contractors are required to review STIGS for applicability, but may not have access to them. Who can provide/justify access? | None
2 | 1.4.4, 3.3.1.2, 3.3.6 | Definitions, User Accounts, Pysical Security in MODERATE Impact Systems | SO, PS | Several Cybersecurity requirements vary depending on whether the item is inside "mission space". Coordinate to determine bounardies of mission space and indicate on contract requirements. Coordinate with physical security designer to ensure requirements are included. | Drawings indicating boundary of misison space to define where different requirements are applicable.
3 | 1.4.11, 3.3.1.2 | Defintions, User Accounts | SO | Many Cybersecurity requirements related to User Interfaces (Uis) depend on whether the UI is "privileged". Coordinate with the SO to determine which UIs are privileged. | Drawings indicating UI privilege.
4 | 3.3.1.2.X | Controllers (User Accounts) | SO, O&M | Coordinate with the site to determine the proper requirements in the User Interface tables. For example, in LOW impact HVAC systems, do Local Limited, Non-privileged Uis need to MINIMALLY support accounts? | 3.3.1.2.x Requirements for User Account access control
5 | 1.5.2, 1.6, 3.2, 3.2.3.3 | Coordination, Submittals, Network Requirements, Wireless and Wired Broadcast Communication Request | SO | The specification requires a pre-construction submittal to approve wireless. It might be useful to discuss wireless with the site prior to finalizing the specification; if they are strongly opposed then the spec could be edited to indicate that. | 3.2.3 Wireless vs wired broadcast preference. 3.2.3.1 Wireless or wired broadcast IP networks. 3.2.3.3 Wireless and Wired Broadcast Communication Request
6 | 1.6 | Submittals | Cyber? | Unlike normal controls submittals, review of cybersecurity submittals requires expertise in cybersecurity and may also require approval from the AO. Coordinate with the SO and Cybersecurity POC to detemine who will review submittals. | Potentially include additional reviewers in Section 1.6.
7 | 1.9.2 | Cybersecurity Interconnection Schedule | SO | If the system connects to another system, who is the point of contact for the other (foreign) system? While the specification requires the contractor to provide this information, they may require goverment assistance in making this determination. | None
8 | 1.9.4 | Control System Inventory Report | SO, Cyber? | Should the Control System Inventory Report include non-networked devices? Coordinate with submittal reviewers identified above | Devices to be include in report
9 | 1.9.6 | Cybersecurity Riser Diagram | SO, Cyber? | Is there a specific format required for the Cyber Riser Diagram? Coordinate with submittal reviewers identified above | Format of report
10 | 1.9.8 | Control System Cybersecurity Documentation | SO | There are likely incomplete submittals on the Control System Cyber Documentation. Coordinate with submittal reviewers identified above to determine how exceptions will be handled. | None
11 | 1.10 | Software Licensing | SO | How long should software be licensed for? What organization should the software be licensed to? | Licensing Requirements
12 | 2.1, 3.2.1, 3.2.7 | Ethernet Switch, Information Flow Enforcement in MODERATE Impact Systems, | SO, IT | From a control system functional perspective, there are essentially no additional requirements on Ethernet switches, a $40 switch from (e.g.,) Best Buy will likely work just fine. The site may have additional requirements to support Cybersecurity. What are those requirements? | 2.1 Ethernet switch product functionality 3.2.1 Configuration of port blocking in Ethernet switches 3.2.7 Requirements to use 802.1x (which likely requires switch support as well).
13 | 2.3 | Database and Web Server Software for MODERATE Impact Systems | IT | Use of "standard" database servers and web servers on computers can facilitate cybersecurity since the site is generally more familiar with standard software packages. Which software packages are allowed by the site for MODERATE systems? | 2.3 Allowed database server and web server software.
14 | 3.2.2 | Wireless and Wired Broadcast Communication for Fire Protection Systems | FM | For Fire Protection (FP) systems, the local BCS may use a radio to communicate with the basewide system. Is there a requirement that the radio meet FIPS 140-2? | Require or not require that radios meet FIPS 140-2.
15 | 3.2.3.4 | Wireless Communication Testing | SO, IT | Determine requirements for wireless testing procedures | 3.2.3.4 Determine testing requirements.
16 | 3.2.3 | Wireless and Wired Broadcast Communication for Systems Other than Fire Protection Systems | SO, IT | For non-Fire Protection systems, will the site permit wireless (or wired broadcast) communication media? | 3.2.3 Preference (or not) for wired broadcast vs wired. 3.2.3.1 Possible option for IP network.
17 | 3.2.6 | Cryptographic Protection | SO, IT | The site may have additional requirements for encryption (beyond use of HTTPS as described). Coordinate with site to determine whether to include these requirements. | 3.2.6 Determine additional requirements for encryption.
18 | 3.3.2 | Unsuccessful Logon Attempts | SO, O&M | To what extent should User Interfaces lock the interface after unsuccessful login attempts, for how long, and how should the lock-out be released? Are there specific interfaces that, because of high availability requirements, should not be locked? | 3.3.2.1 & 3.3.2.2 Device Lock requirements 3.3.2.3 Any interface exempt from these requirements
19 | 3.3.4 | Session Lock and Session Termination Requirements in MODERATE Impact Systems | SO, O&M | For MODERATE systems, how soon should session lock be initiated after cessation of activity? How about for session termination? Are there exceptions? | Define requirements in 3.3.4.3, 3.3.4.4, and 3.3.4.5.
20 | 3.3.5 | Permitted Actions Without Identification or Authentication | SO, O&M | Can read-only actions be performed from a UI (that supports accounts) if a user is not logged in? | 3.3.5 Determine if read-only actions are permitted
21 | 3.3.6.4 | Additional Physical Security for Confidentiality of User Interface and Printers | SO, O&M | Are there any User Interfaces which require protection because of Confidentiality concerns in the system? | 3.3.6.4 Add additional requirements if required.
22 | 3.4.1, 3.4.2 | User Identification and Authentication for All System Types/Specific System Types | SO, IT | Are there any requirement for multi-factor authentication (typically PIV or CAC)? Note that this requires extensive site support. Are there user interfaces with specific requirements? | 3.4.1 and 3.4.2 Add additional requirements for use of PIV.
23 | 3.4.3 | User Identification and Authentication for Specific Devices | SO, O&M | Are there specific devices that have specific requirements | Fill out the table
24 | 3.4.5 | Password-Based Authentication Requirements | SO, O&M | There may be some devices that cannot meet stated password requirements. The default is to reject those devices; does the SO have any preferences? | None
25 | 3.4.5.5 | Password Configuration and Reporting | O&M | Would the site prefer a report providing the device passwords, or would the site prefer to have a person accompany the contractor and change the passwords themselves? | Select the approach to password configuration
26 | 3.4.7 | Implelmentation of PKI Infrastructure in MODERATE Impact Systems | SO, IT | Does the site want the contractor to help set up PKI infrastructure in the system | Include requirements for PKI support.
27 | 3.5 | Cybersecurity Audting | SO | In some cases, the "preferred" system may not be able to meet all the required auditing requirements. What is the AO's position on this issue? | None.
28 | 3.5.3 | Auditing Front End Software | SO, IT | Regarding Auditing Front End Software: Does the site have existing software? What is it? Is it compatible with the provided control system (note this question might require detailed knowledge of the control system and not be aswerable by other than the controls vendor)? | Edit requirements for auditing front end software.
29 | 3.5.3 | Auditing Front End Software | SO, IT | If separate Auditing Front End Software is provided, where should it be installed? | Edit installation requirements for audit front end software.
30 | 3.5.3.4 | Audit Reduction and Report Generation in MODERATE Impact Systems | SO | What is the maximum time stamp discrepancy that the auditing reduction software can account for? | Edit requirements.
31 | 3.5.4 | Audit Storage Capacity and Audit Upload | SO | For controllers and computers, how many audit records should those devices be able to store locally at the device? | Edit requirements.
32 | 3.5.5 | Response to Audit Processing Failures | SO | How should the system respond to auditing processing failures? | Edit requirements.
33 | 3.6 | Requirements for Least Functionality | CD | Coordinate with other design disciplines to ensure the system does not have unnecesary capabilities. | None in UFGS 25 05 11, possible impacts in other control specs and drawings.
34 | 3.7.1 | Collaborative Computing | SO, IT | If there is a desire for the control system to use collaborative computing, who would approve this? Do they approve this? | None.
35 | 3.7.5 | Process Isolation and Boundary Protection in Moderate Impact Fire Protection Systems. | FM | For MODERATE Fire Protection (FP) systems, radios that do not meet FIPS 140-2 have additional requirements to isolate them from the FP system. Some of these requirements may reduce desired functionality. Which particular requirements doe sthe site desire? | Edit requirements.
36 | 3.8 | Safe Mode and Fail Safe Operation | SO, CD | Coordinate with SO and other design disciplines to ensure that safe mode and fail-safe operation is designed into the system. | None in UFGS 25 05 11, possible impacts in other control specs and drawings.
37 | 3.9 | System Maintenance Tool Software | SO, O&M | How many copies (and what format) does the site desire for the system maintenance tool software? | Edit requirements.
38 | 3.10 | Device Power | SO, CD, CE | Cybersecurity requirements for control system power need to be coordinated with power for the controlled equipment. Keeping the control system powered is of no value if the controlled equipment has failed for some intrinsic (e.g., broken belt) or extrinsic (e.g., loss of power) reason. Coordinate with other disciplines to ensure that similar levels of availability are provided for all aspects of the overall system. | None.
39 | 3.13.1 | Malicious Code Protection | SO, IT | Does the system need malware protection software licenses, software media, neither, or both? In many cases, the site will have specific requirements. Coordinate with the site to determine their requirements. | Edit requirements.
40 | 3.13.3 | Information System Monitoring | SO, IT | Specific sites (particularly for MODERATE systems) may have additional requirements for information system monitoring. Coordinate with the site to determine these requirements. | Include requirements if necessary.
41 | 3.14 | Control System Cybersecurity Testing | SO | Coordinate with the site for number of copies of the Cybersecurity testing procedures and test report. | Edit requirements for number of copies of reports.
42 | 3.15 | Field Quality Control, Cybersecurity Validation Support | SO, IT | Coordinate with the site to determine the number of hours that the contractor should allot for their participation in RMF validation testing. Note that this is a separate task from the cybersecurity testing in 3.14. | Edit requirements to determine number of hours required.
43 | 3.16 | Cybersecurity Training | SO, O&M | How much cybertraining does the site want? | Edit requirements to determine number of hours required.
Note on C4: This Section refers to Security Requirements Guide (SRGs) and Security Technical Implementation Guide (STIGs). STIGs and SRGs are available online at the Information Assurance Support Environment (IASE) website at https://public.cyber.mil/stigs/downloads/ and an SRG/STIG Applicability Guide and Collection Tool is available at https://public.cyber.mil/stigs/SCAP/.
Note on C5: 1.4.4 Mission Space ************************************************************************** NOTE: Define "Mission space" such that the contractor is able to determine when a network or device is outside of the mission area. Coordinate the definition of Mission Space with the physical security design and the security organization at the project site. Select whether to leave the definition or to define mission space on a drawing. ************************************************************************** [A device or media is in mission space if physical access to the device or SECTION 25 05 11 Page 12media is controlled by the organization served by the device. For example, a VAV box controller in a suspended ceiling is in mission space if the VAV box serves that room; an electrical switchgear in an electrical room or an AHU in a mechanical room or on a rooftop may still be considered to be in mission space if the organization (mission) served by that switchgear or AHU controls access to the electrical room, mechanical room or rooftop.][Mission space is shown on the drawings.]
Note on C6: 1.4.11.4.2 Privileged User Interface ************************************************************************** NOTE: This subpart uses tailoring options for the lettered requirements. After selecting tailoring options edit the letters in this subpart accordingly. ************************************************************************** A Privileged UI is a UI that has sufficient capabilities or functionality that it requires specific cybersecurity measures to be put in place to limit its unauthorized use. Ultimately, whether a specific user interface is considered a Privileged User Interface must be determined by usage. Unless otherwise specified, user interfaces can be determined to be privileged or not using the following: <SEE SPEC FOR MORE DETAILS>
Note on C7: <SEE SPEC FOR MORE DETAILS>
Note on C8: 1.5.2 Coordination … a. If requesting permission for wireless or wired broadcast communication, the Wireless and Wired Broadcast Communication Request submittal must be approved prior to control system device selection and installation.
Note on C9: <SEE SPEC FOR MORE DETAILS>
Note on C10: [1.9.2 Cybersecurity Interconnection Schedule ************************************************************************** NOTE: The Cybersecurity Interconnection Schedule is used in two situations: 1) The control system communicates with a separately authorized system or an unauthorized system. In this case, include a Cybersecurity Interconnection Schedule in the design showing the following interconnection details: Name/description of other system, POC for the other system, type of data/information. 2) The control system is a sub-part of a larger system and will communicate with and integrate to the larger system (and will be part of the same authorization as the larger system). In this case, the control system design must include requirements for the expected communication between the sub-system and the larger system. The Cybersecurity Interconnection Schedule will not be a design drawing, but will still be a contractor submittal. If neither of these situations apply (if the system is stand-alone with no connection or integration to another system), remove the bracketed text requiring the Cybersecurity Interconnection Schedule, and remove the Cybersecurity Interconnection Schedule from the SUBMITTALS paragraph of this Section. If Case 1 applies, keep the bracketed text referring to Foreign Destination and POC for Destination, otherwise remove this text. In situations where both cases apply, a single submittal will serve both purposes. Note that this submittal does not create a requirement for interconnections, but documents interconnection details in accordance with other requirements. ************************************************************************** ... Provide a completed Cybersecurity Interconnection Schedule documenting network connections between the installed system and other systems. Provide the following information for each device directly communicating between systems: Device Identifier, Device Description, Transport layer Protocol, Network Address, Port (if applicable), MAC (Layer 2) address (if applicable), Media, Application Protocol, Service (if applicable), Descriptive Purpose of communication. [For communication with other authorized systems also provide the Foreign Destination and POC for Destination.]
Note on C11: 1.9.4 Control System Inventory Report ************************************************************************** NOTE: Select whether the inventory report must include non-networked devices. Unless specifically required by the project, keep the first bracketed text to require inventory of only networked devices and remove the later bracketed text requiring inventory of non-networked devices, input devices and output devices. ************************************************************************** ... Provide a Control System Inventory report using the Inventory Spreadsheet listed under this Section at https://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/ufgs-25-05-11 documenting all [networked devices, including network infrastructure devices][devices, including networked devices, network infrastructure devices, non-networked devices, input devices (e.g. sensors) and output devices (e.g. actuators)]. For each device provide all applicable information for which there is a field on the spreadsheet in accordance with the instructions on the spreadsheet.
Note on C12: 1.9.6 Cybersecurity Riser Diagram ************************************************************************** NOTE: Select or specify the format for the riser diagram. ************************************************************************** ... Provide a cybersecurity riser diagram of the complete control system including all network and device hardware. If the control system specifications require a riser diagram submittal, provide a copy of that submittal as the cybersecurity riser diagram. Otherwise, provide a riser diagram in [one-line format][one-line format overlayed on a facility schematic][tabular format][_____].
Note on C13: 1.9.8 Control System Cybersecurity Documentation ************************************************************************** NOTE: The following enumerates very detailed requirements for documentation; requirements that would be impossible to meet for some control devices.
Note on C14: 1.10 SOFTWARE LICENSING ************************************************************************** NOTE: The installation may procure its own software update licensing or contract and thus needs less than 5 years. Alternatively, the installation may require longer than five years (although this will likely increase the costs significantly). Coordinate with the installation to determine if they have any specific requirement; if they don't then keep the 5 year requirement. Note that this requirement may already exist in the control system specifications, in which case it can removed from this Section (or kept in this Section and removed from the control system specification). ************************************************************************** For all software provided that has not already been licensed to the government or project site, provide a license to the [Government][project site][_____] for a period [of no less than 5 years][___], and the license must also include the following software updates:
Note on C15: 2.1.1 Required Functionality ************************************************************************** NOTE: Include bracketed options which correspond to required switch functionality, and change bullet letters accordingly. Determine functionality in coordination with the system owner organization and do not include any requirements that are not specifically needed. Use particular caution in requiring IEEE 802.1x as most controllers will not support it.
Note on C16: 2.3 DATABASE AND WEB SERVER SOFTWARE FOR MODERATE IMPACT SYSTEMS ************************************************************************** NOTE: Indicate the permitted database and web servers. ************************************************************************** All computer-based databases must use [Microsoft SQL Server][ or ][Oracle][ or ][MySQL]. All computer-based web interfaces must use [Internet Information Services (IIS)][ or ][Apache] as the web server.
Note on C17: 3.2.2 Wireless and Wired Broadcast Communication for Fire Protection Systems ************************************************************************** NOTE: Indicate whether the communication from a facility fire protection system to the central monitoring station must meet FIPS 140-2. Coordinate this requirement with the project site, and if the existing system does not use FIPS certified radios and it is not certain the existing system is able to employ FIPS certified radios DO NOT include this requirement. Note that mitigation measures for non-FIPS 140-2 radios are covered in "Process Isolation and Boundary Protection in Moderate Impact Fire Protection Systems" ************************************************************************** The use of wireless and wired broadcast communication for fire protection systems within a facility is prohibited. Wireless communication may be used to provide communication from the fire protection system in a facility to the central monitoring station. [Communication between the fire protection system and the central monitoring station must be via FIPS 140-2 certified devices.]
Note on C18: 3.2.3.4 Wireless Communication Testing ************************************************************************** NOTE: Select or enter appropriate name for the system-level test of the control system. Select or indicate the wireless network test boundary. ************************************************************************** As part of [Performance Verification Testing (PVT)][Functional Performance Testing {FPT}][___], conduct testing of wireless communication for all devices indicated on the approved Wireless and Wired Broadcast Communication Request as requiring testing. To test wireless communication, test for wireless network reception at multiple points along the wireless test boundary in the vicinity of the wireless device, and record whether a network connection can be established at each point. The wireless test boundary is [the building exterior walls][the facility fence line][_____].
Note on C19: <SEE SPEC FOR MORE DETAILS>
Note on C20: <SEE SPEC FOR MORE DETAILS>
Note on C21: 3.3.2 Unsuccessful Logon Attempts ************************************************************************** NOTE: Note that most field devices that only MINIMALLY support accounts (e.g. a Local Display Panel) cannot be locked. Keep the bracketed text requiring that these devices lock ONLY if this is a specific project requirement. If keeping this text, include requirements on when the interface must lock and how to unlock. Some unlocking conditions to consider are: network command or a physical button which is protected by a locked enclosure. Note that a requirement for a HIGH availability at the front end may preclude locking out an account for failed logon attempts. If the system includes high availability user interfaces which should not be locked, include the bracketed text exempting high availability interfaces and keep the bracketed table. Indicate in the table the exempt interfaces, their location and action to take for each in lieu of locking the screen. Use care with high availability user interfaces, as in most cases the control system should act without user intervention, and a high availability user interface depends on a "high availability" operator.
Note on C22: 3.3.4 Session Lock and Session Termination Requirements In MODERATE Impact Systems: ************************************************************************** NOTE: Indicate duration of inactivity before terminating or locking a session. Also indicate the maximum number of concurrent sessions to prevent a single user from being logged in multiple ("too many") times. **************************************************************************
Note on C23: ]3.3.5 Permitted Actions Without Identification or Authentication ************************************************************************** NOTE: These requirements are specifically about user actions, not actions taken automatically by control system components. Unless there is a project-specific confidentiality concern or other project-specific requirement keep the bracketed text "except read only actions". Notes concerning how this requirement addresses cybersecurity when bracketed text "except read only actions" is NOT included: 1) This requirement indicates that there are no actions that can be taken without identification and authentication for any user interface where account support is required. 2) This requirement does not limit actions taken by a user on a user interface that does not support accounts, but other requirements limit this to READ-ONLY interfaces. 3) Thus the "permitted actions" referred to by control AC-14 are "read-only access to information from devices which are not required to have user accounts." When "except read only actions" IS included, read-only actions even from devices supporting accounts are permitted without authentication and thus the "permitted actions" referred to by control AC-14 are "read-only access to information" ************************************************************************** The control system must require identification and authentication before allowing any actions[ except read-only actions] by a user acting from a user interface which MINIMALLY or FULLY supports accounts.
Note on C24: 3.3.6.4 Additional Physical Security for Confidentiality of User Interfaces and Printers ************************************************************************** NOTE: If specific user interfaces or printers require additional security controls to protect the confidentiality of the information displayed or printed, keep this Subpart and indicate these requirements in the table. Otherwise remove this bracketed subpart. These additional requirements will generally NOT be required as these are secured due to the multiple MODERATE controls already applied. It's possible additional requirements will be needed for systems containing PII or other sensitive data. Additional controls may include increased physical security, locating shredders/burn bags near printers, and installing privacy screens on monitors. **************************************************************************
Note on C25: <SEE SPEC FOR MORE DETAILS>
Note on C26: 3.4.3 User Identification and Authentication for Specific Devices ************************************************************************** NOTE: If there are specific devices (e.g. "Rm 17 lighting user interface", "all model 17 controllers"), keep the bracketed text including the table and list them along with the required methods in the table. Otherwise keep bracketed text indicating there are no device specific user interface requirements ************************************************************************** [ There are no additional device specific user interface requirements][Additional user identification and authentication requirements are defined in the TABLE.
Note on C27: <SEE SPEC FOR MORE DETAILS>
Note on C28: 3.4.5.5 Password Configuration and Reporting ************************************************************************** NOTE: Select whether the contractor will change passwords and submit a copy of the passwords or accompany site personnel while they change passwords. In the case of contractor changing the passwords: Provide a POC for password coordination. This will generally be a supervisor or other senior member of the project site maintenance organization. The Password Summary Report is needed by the project site system owner or O&M staff. This report is required to be delivered as hardcopy in a sealed envelope to keep passwords more confidential. Note that the contractor will know the passwords, so there remains a risk, but by changing the default the number of individuals knowing the password for a specific device is greatly reduced (from "everyone" to "the contractor and the installation") In the case of site personnel changing the passwords, indicate the POC for coordination. **************************************************************************
Note on C29: 3.4.7 Implementation of PKI Infrastructure in MODERATE Impact Systems ************************************************************************** NOTE: For MODERATE Impact Systems: Most systems will not use PKI (typically implemented as PIV (CAC) authentication). If PKI is supported at the front end, it may be implemented by the basewide network (Platform Enclave) and not the controls contractor. If there is a requirement for the contractor to support PKI, include this subpart, otherwise remove it. Note, PKI Infrastructure is not required to supportthe requirement for use of HTTPS for remote user interfaces. **************************************************************************
Note on C30: <SEE SPEC FOR MORE DETAILS>
Note on C31: 3.5.3 Auditing Front End Software ************************************************************************** NOTE: Auditing Front End Software may be a component of the control system front end or a separate software package. In either case - but particularly when it is part of an existing control system front end -- the site may already have this software. Confirm with the project site whether they already have this software. If they do, indicate the current software. Use the bracketed text to indicate where software is to be installed (either on the control system front end computer or indicate another computer) or to require that the software be provided for installation by the project site. ************************************************************************** The project site currently has the following software to support control system auditing: [none][_____]. If there is no existing auditing front end software or the software is not compatible with the provided control systems, provide Auditing Front End Software with audit log import and upload, export, notification, and analysis functionality. The Auditing Front End Software may be provided as a component of the control system front end or as a separate software package, and a single package may serve multiple control systems provided under the same projects if they are sharing a cybersecurity authorization. When the Auditing Front End Software is neither existing nor installed under the requirements of another Section, furnish the Auditing Front End Software media and license [for subsequent Government installation][and install the software on [_____]][the control system front end computer in [_____]] Submit copies of Auditing Front End Software if this function is not part of the software provided with the control system to meet requirements of other Sections.
Note on C32: <See above note>
Note on C33: 3.5.3.4 Audit Reduction and Report Generation In MODERATE Impact Systems ************************************************************************** NOTE: Indicate the time stamp discrepancy between audit logs that the system must be able to accommodate for correlating audit logs. This accounts for timestamp errors between different auditing devices, and will allow for multiple entries to be linked to the same event. The 2-second default is based on the time stamp accuracy requirement in the Time Stamps subpart, and accounts for device clocks being plus or minus 1 second (total of a 2 second span). **************************************************************************
Note on C34: 3.5.4 Audit Storage Capacity and Audit Upload ************************************************************************** NOTE: Select or indicate duration and rate of audit record generation for field devices. Unless there is a known need, do not add requirements for computer storage capability. *************************************************************************
Note on C35: 3.5.5 Response to Audit Processing Failures ************************************************************************** NOTE: The requirement that audit processing failures notify a person implies that this control can only be met at a computer with network access, not by a control device within the control system. The action taken should be "overwrite oldest audit records" if possible; it should almost certainly never be "shut down information system". Provide a POC to notify, either the Security Controls Assessor (SCA) or the Information System Security Officer (ISSO). Provide a default action. **************************************************************************
Note on C36: 3.6 REQUIREMENTS FOR LEAST FUNCTIONALITY ************************************************************************** NOTE: The control system should be designed to have the least capability possible while still meeting the minimum needs of the government. This means disabling unnecessary functionality. Do not install unnecessary software. Ensure that unnecessary accounts, maintenance passwords, etc. are all changed, disabled, or removed. For systems other than HVAC control systems: Consider disallowing unrequested user interfaces and consider disallowing networked sensors/actuators where they are not required. **************************************************************************
Note on C37: 3.7.1 Collaborative Computing Without explicit approval from the project site, control systems must not use collaborative computing technologies.
Note on C38: 3.7.5 Process Isolation and Boundary Protection in Moderate Impact Fire Protection Systems ************************************************************************** NOTE: For many FRCS (Fire Protection being a notable exception), implementation of boundary protection is typically outside the scope of the controls contractor. The site IT staff should implement boundary protection via rules (e.g. a firewall) isolating the control system from the wider network. This is true even for a control system which will be later integrated to a larger system; the field point of connection (FPOC) should be configured to allow the minimum traffic necessary for operation. Critical to this is the Cybersecurity Interconnection Schedule, which defines what traffic must be allowed through the boundary for the proper operation of the system. For Fire Protection Systems, some aspects of boundary protection are likely the responsibility of the installing contractor. In general, the ability to play a live audio message will be required and include the bracketed text. However, in many cases, the ability to play live audio is a vulnerability and in some cases, the site may not be willing to accept the risk. Coordinate with the site to determine whether to allow this functionality. Select whether relays must use the normally open or normally closed contact. If a code requirement exists, follow the code. Otherwise coordinate with the fire protection specification and the project site and consider whether the greater risk is the potential to send a message when none should be sent, or the failure to send a message when one should be sent. If it is clear that one case is of greater concern than the other, select the appropriate bracketed text, otherwise remove the bracketed text to not introduce a specific requirement. Coordinate requirements with those of "Safe Mode and Fail Safe Operation" in the following paragraph. **************************************************************************
Note on C39: 3.8 SAFE MODE AND FAIL SAFE OPERATION ************************************************************************** NOTE: The designer should determine, based on the criticality of the controlled equipment, what conditions to consider and which actions, if any, including possible alarm requirements, the control system should take when these conditions are true. This should include external conditions (e.g. loss of off-site utility power), internal conditions (e.g. network or sensor failure), and operator input (e.g. manual command to a safe mode of operation). This should all be specified in the control logic (e.g. sequence of operations), in particular by addressing normal/failed positions of output devices, including default positions upon loss of network, and in the overall system design. Where high reliability is required, the analysis should consider the addition of redundant equipment to the design. See also guidance on SC-24 (Fail in Known State), guidance on SI-17 (Fail-Safe Procedures) and the MINIMUM CYBERSECURITY DESIGN REQUIREMENTS in UFC 4-010-06, Cybersecurity for Facility-Related Control Systems. Note that any requirements in the control system needed to meet CP-12 (Safe Mode) or SI-17 (Fail-Safe Procedures) should be specified in existing specifications and design, for example, redundant AHUs in the mechanical design and sequences of operation. Any specific requirements for CP-12 or SI-17 should be addressed in those sections, not in this UFGS. *************************************************************************
Note on C40: 3.9 SYSTEM MAINTENANCE TOOL SOFTWARE ************************************************************************** NOTE: Indicate the number of hardcopy manuals required. ************************************************************************** Submit and license to the Government all software required to operate, maintain and modify the control system such the Government or their agents are able to perform repair, replacement, upgrades, and expansions of the system without subsequent or future dependence on the Contractor, Vendor or Manufacturer. Submit hard copies of user manuals for each software with the software submittal. For software provided and licensed to the Government under the requirements of another Section, submit a statement indicating the Section and Submittal under which the software was provided. For software provided to meet the requirements of this Section and not provided and licensed under another Section, submit software and software user manuals on DVD or CD as a Technical Data Package and submit [one hard copy][[_____] hard copies] of the software user manual for each piece of software.
Note on C41: 3.10 DEVICE POWER ************************************************************************** NOTE: A long term alternate power supply is almost never required by the control system itself (independent of the controlled equipment). Alternate long term power, if required, will be because of a tenant requirement or by the overall system design and should seldom be added as an ad-hoc requirement. Control systems for underlying systems with alternate power should use that alternate power source. A UPS may be desired for specific control system components where rapid recovery after a power outage is required, or where the control system itself is necessary for restoration of power. Again, this should be driven by mission requirements and control system specifications should already require adequate system restoration after loss of power. If there are specific requirements for either short-term (UPS) or long-term (generator or alternate power source), include them as part of the design and in the relevant specification sections rather than adding requirements to this section. Note that use of small local UPSes creates additional maintenance burdens due to the requirements for periodic battery replacement and may ultimately result in a less reliable system. For MODERATE Impact Systems: This is a particularly important consideration and designers are strongly cautioned against small per-controller UPS and recommended to use a central UPS instead. Brackets are provided here for the EXTREMELY RARE case in which emergency power requirements must be specified here. In most cases, keep the bracketed text indicating emergency power requirements are in accordance with the control system and equipment specifications. For MODERATE Impact Systems: As the system has a MODERATE impact there is a particularly strong presumption the mission already requires and is providing emergency power, and the control system should therefore use the same emergency power as the underlying equipment. ************************************************************************** ************************************************************************** NOTE: For MODERATE Impact Systems, the requirement is for redundant power cabling paths. For this to result in significantly increased availability, the paths must be fed from independent power sources (i.e. the cable paths must be redundant all the way back to redundant power sources). Coordinate with the electrical designer to see if this level of power redundancy has been designed into the system. If this level of redundancy is required for availability, coordinate with the designer of the controlled equipment (e.g., for HVAC controls, coordinate with the HVAC system designer) to determine if there is a requirement for redundant controlled equipment as well - redundant power to a single piece of controlled equipment still has a single point of failure at the controlled equipment. The specification requirement covers these issues by simply requiring the controller power to be as reliable as the equipment power. If there is no requirement for redundant (controlled) equipment power or redundant (controlled) equipment, then there is little value in trying to provide redundant power to the control system as the most likely failures are mechanical or electrical failures in the controlled equipment or loss of equipment power, not independent loss of power to the control system. Note that sequences of operation often lock out equipment in case of failure. Consider carefully how to address general loss of power to ensure that automatic recovery after loss of power is possible. **************************************************************************
Note on C42: 3.13.1 Malicious Code Protection ************************************************************************** NOTE: Malware protection software media may be government or contractor furnished; it may be either Government or contractor installed, and the license may be government or contractor furnished. For each of media, license and installation select the bracketed text indicating contractor or Government responsibility. ************************************************************************** For all computers installed under this project, provide malware protection software media, provide licenses, and install and configure malware protection software as indicated. Coordinate with the Government Computer Access Point of Contact as required. a. [Provide malware protection software licenses.][Malware protection software licenses will be Government furnished.] b. [Provide malware protection software media.][Malware protection software media will be Government furnished.] c. [Install and configure malware protection software in accordance with the relevant STIGs.][Malware protection software will be Government installed.]
Note on C43: 3.13.3 Information System Monitoring ************************************************************************** NOTE: Delete this subpart unless specifically required for the project. If required, indicate requirements for the monitoring of the control system. ************************************************************************** [_____]
Note on C44: 3.14.1 Control System Cybersecurity Testing Procedures Prepare Control System Cybersecurity Testing Procedures explaining step-by-step, the actions and expected results that will demonstrate that the control system meets the requirements of this Section. Submit [4] [_____] copies of the Control System Cybersecurity Testing Procedures. The Control System Cybersecurity Testing Procedures may be submitted as a Technical Data Package. 3.14.2 Control System Cybersecurity Testing Execution Using the Control System Cybersecurity Testing Procedures verify that the control system meets the requirements of this Section. UNLESS GOVERNMENT WITNESSING OF A TEST IS SPECIFICALLY WAIVED BY THE GOVERNMENT, PERFORM ALL TESTS WITH A GOVERNMENT WITNESS. If testing reveals deficiencies in the system, correct the deficiency and retest until successful. 3.14.3 Control System Cybersecurity Testing Report Prepare and submit a Control System Cybersecurity Testing Report documenting all tests performed and their results. Include all tests in the Control System Cybersecurity Testing Procedures and any additional tests performed during testing. Document test failures and repairs conducted with the test results. Submit [four][_____] copies of the Control System Cybersecurity Testing Report. The Control System Cybersecurity Testing Report may be submitted as a Technical Data Package.
Note on C45: 3.15 FIELD QUALITY CONTROL, CYBERSECURITY VALIDATION SUPPORT ************************************************************************** NOTE: Coordinate with the entity performing cybersecurity testing to determine support requirements for cybersecurity testing. Some possible values to consider: 1) A control system with no IP devices: 1-2 days. 2) A control system with IP devices: 5 days 3) If the system includes a new front-end (server): +5 additional days ************************************************************************** In addition to testing and testing support required by other Sections, provide a minimum of [_____] hours of technical support for cybersecurity testing of control systems to support the DoD Risk Management Framework process Cybersecurity assessment of the control system. This support is independent of (and in addition to) the Control System Cybersecurity Testing specified in this section.
Note on C46: 3.16 CYBERSECURITY TRAINING ************************************************************************** NOTE: Indicate the number of hours of training and number of attendees. Unless training is specifically waived by the project site, DO NOT remove training requirements. ************************************************************************** Provide [eight][__] hours of classroom[ and hands-on] training for [six][__] Government personnel on the cybersecurity operation and maintenance of the control system provided. This training is in addition to and must be coordinated with control system training specified in other Sections.