## Instructions
Interconnection Schedule
Document connections between this control system and other systems.
Designer should generate this schedule as part of design. Designer should always provide the "Descriptive Purpose" and "Foreign Destination"; depending on the project, designer may provide other details as well.
Contractor should complete the table, but may need outside input for the Network Address
Device ID should be a key to an entry in the <Inventory Table>
Network Address relates to the Transport Layer protocol and is typically the IP address.
Transport Layer protocol will typically be IP, provide if something other than IP.
Protocol is the application level protocol -- eg. SMTP, Lon.
Service might be a protocol-specific service -- eg BACnet Confirmed File Transfer
Network Comunication Schedule
This documents connections within the control system.
This information may already be contained on other submittals, in which case those documents may be submitted instead.
(For HVAC installed IAW 23 09 00 it is contained on the Point Schedules.)
Wireless
Prior to using wireless, contractor must submit a Wireless Communication Request schedule with columns A - I filled out.
Govt. will Approve or Disapprove in column J. Approved devices may require post-installation testing.
For devices requiring post-installation testing, contractor shall attempt network connectivity at various points and document (Yes/No, Pass/Fail) whether network connectivity existed
Multiple IP Connection
Prior to using a device with multiple IP connections, contractor must submit a Multiple IP Connection Device Request schedule with columns A - G filled out.
Govt. will Approve or Disapprove in column H.

## Interconnect
Device ID | Device Description | Foreign Destination | POC for Destination | Transport layer Protocol | Network Address | Port (if applicable) | MAC (Layer 2) address (if applicable) | Media | Application Protocol | Service (if applicable) | Descriptive Purpose
UMCS M&C Server | UMCS M&C Server | Exchange Server | <IT email POC> | IP | 10.0.5.23 | TCP/25 | 00:26:B9:B5:A5:34 | Cat 6 | SMTP | NA | email to email-to-SMS service for alarm messaging | This is a sample entry for a UMCS front end IAW UFGS 25 10 10
DDC-5 | AHU-5 Controller | UMCS Front End | <Energy Manager> | IP | 192.168.45.3 | UDP/0xBAC0 | 12:34:56:78:9A:BC | Cat 5 | BACnet | multiple | Trend upload, interactive data sharing with M&C server, alarms | These are sample entries for a HVAC building control system IAW UFGS 23 09 00 designed to communicate to a separate front end
DDC-8 | Chiller Controller | UMCS Front End | <Energy Manager> | IP | 192.168.45.78 | UDP/0xBAC0 | DE:F0:12:34:56:78 | Cat 5 | BACnet | multiple | Trend upload, interactive data sharing with M&C server, alarms
DDC-3 | Supervisory Controller | UMCS Front End | <Energy Manager> | IP | 192.168.45.34 | UDP/0xBAC0 | 9A:BC:DE:F0:12:34 | Cat 5 | BACnet | Read Property, Write Property | Used by front end for demand limiting in building
DDC-6 | Lighting Gateway | Lutron Lighting Gateway | <Lighting system owner> | Lon | 2, 34, 12 (Domain, Subnet, Node) | NA | AF23:8456:B8D3 (Neuron ID) | TP/FT-10 | Lon | NA | Communicate occupancy status with lighting system | Sample entry for a HVAC system which shares occupancy data with a lighting system via Lon

## Network Comm
Device ID | Device Description | Transport layer Protocol | Network Address | Port (if applicable) | MAC (Layer 2) address (if applicable) | Media | Application Protocol | Service (if applicable) | Descriptive Purpose

## Wireless
Network connectivity at required points (Y/N)?
Device ID | Device Description | Location | Receiving Device IDs | Protocol | Encryption (type / bits) | RF Frequency | Radiated Power (dBm) | Free-space range | As-installed range | Approved (Y/N) | Testing Required (Y/N) | Location 1 | Location 2 | Location 3 | …. | Location <n>

## Multiple_IP
Device ID | Device Make and Model | Device Description (Include Device Function) | Location | Network 1 Identifier or Description | Network 2 Identifier or Description | Justification for Multiple Connections | Approved (Y/N)