EQUIPMENT TESTS

04/18

PROJECT:	________________________________________________________________

LOCATION:     _________________________________________________________________

To be performed after flushing, cleaning, and control valve and electrical component adjustments

ITEM 1 – R12 (HHT1) CAPABILITIES

| EQUIPMENT – TRUCK NO. _______ |  | ADJUST AND VERIFY |  |
| --- | --- | --- | --- |
|  |  | ACTION | VALUE |
| CONTROL VALVE |  | CLOSURE RATE (SEC), DEADMAN RELEASE |  |
| CONTROL VALVE |  | NOZZLE PRESSURE SET POINT (PSI) |  |
| CONTROL VALVE |  | NOZZLE PRESSURE SET POINT (SEC), SURGE |  |
| CONTROL VALVE |  | CLOSURE RATE (SEC), DURING SURGE |  |
| VENTURI |  | CALIBRATED TO DESIGN FLOW |  |
| SURGE SUPPRESSOR FRONT |  | PROPERLY CHARGED AND WORKING |  |
| SURGE SUPPRESSOR REAR |  | PROPERLY CHARGED AND WORKING |  |
| PRESSURE GAUGE, GROUND NOZZLE |  | CALIBRATED |  |
| PRESSURE GAUGE, UNDERWING NOZZLE |  | CALIBRATED |  |
| DEFUEL |  | FLOW (GPM) |  |
| DEFUEL |  | PRESSURE (PSI) |  |
| DEFUEL |  | OPERATION |  |
| HYDRANT PRESSURE GAUGE |  | CALIBRATED |  |
| AIR SENSE PRESSURE GAUGE |  | CALIBRATED |  |
| GROUND HOSE 1 |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| GROUND HOSE 2 |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| GROUND HOSES COMBINED |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| UNDERWING HOSE 1 |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| UNDERWING HOSE 2 |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| UNDERWING HOSES COMBINED |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| + No tests to be repeated for Performance Testing |  |  |  |  |
| DATE: |  |  |  |  |
| TIME: |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |

ITEM 1 – R12 (HHT2) CAPABILITIES

| EQUIPMENT – TRUCK NO. _______ |  | ADJUST AND VERIFY |  |
| --- | --- | --- | --- |
|  |  | ACTION | VALUE |
| CONTROL VALVE |  | CLOSURE RATE (SEC), DEADMAN RELEASE |  |
| CONTROL VALVE |  | NOZZLE PRESSURE SET POINT (PSI) |  |
| CONTROL VALVE |  | NOZZLE PRESSURE SET POINT (SEC), SURGE |  |
| CONTROL VALVE |  | CLOSURE RATE (SEC), DURING SURGE |  |
| VENTURI |  | CALIBRATED TO DESIGN FLOW |  |
| SURGE SUPPRESSOR FRONT |  | PROPERLY CHARGED AND WORKING |  |
| SURGE SUPPRESSOR REAR |  | PROPERLY CHARGED AND WORKING |  |
| PRESSURE GAUGE, GROUND NOZZLE |  | CALIBRATED |  |
| PRESSURE GAUGE, UNDERWING NOZZLE |  | CALIBRATED |  |
| DEFUEL |  | FLOW (GPM) |  |
| DEFUEL |  | PRESSURE (PSI) |  |
| DEFUEL |  | OPERATION |  |
| HYDRANT PRESSURE GAUGE |  | CALIBRATED |  |
| AIR SENSE PRESSURE GAUGE |  | CALIBRATED |  |
| GROUND HOSE 1 |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| GROUND HOSE 2 |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| GROUND HOSES COMBINED |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| UNDERWING HOSE 1 |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| UNDERWING HOSE 2 |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| UNDERWING HOSES COMBINED |  | FLOW AND INLET PRESSURE (GPM AND PSI) |  |
| + No tests to be repeated for Performance Testing |  |  |  |  |
| DATE: |  |  |  |  |
| TIME: |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |

ITEM 2 – COMPUTER TESTS

| EQUIPMENT |  | VERIFY |  |  |
| --- | --- | --- | --- | --- |
|  |  | ACTION | YES | NO |
| PLC’s |  | LOGIC IN BOTH PLCs IS EQUAL WHEN COLD STARTED |  |  |
| PLC’s |  | REMOVE POWER FROM BACKUP PLC. INCREASE RUN TIME ON LEAD PUMP. PROVIDE POWER BACKUP PLC AND WITNESS SYNCING RUN TIME. |  |  |
| PCP COOLING FANS AND THERMOSTAT |  | PROPER OPERATION |  |  |
| COMPUTER SCREENS, SYSTEM TEST |  | PRESENT AND OPERATIONAL |  |  |
| ALARM PANEL |  | ALARMS ARE PRESENTED CORRECTLY EX: PUMP 1 FAILURE DISPLAYED ON ALARM PANEL AND ALARM SCREEN |  |  |
| POWER SUPPLY |  | BACKUP POWER IS OPERATIONAL WHEN PRIMARY FAILS |  |  |
| BACKUP PLC |  | SEAMLESS OPERATION WHEN PRIMARY FAILS |  |  |
| PRIMARY PLC (WHEN IN BACKUP MODE) |  | SEAMLESS OPERATION WHEN BACKUP FAILS |  |  |
| BACKUP INPUT/OUTPUT |  | SEAMLESS TAKEOVER WHEN PRIMARY FAILS |  |  |
| PRIMARY INPUT/OUTPUT (WHEN IN BACKUP MODE) |  | SEAMLESS OPERATION WHEN BACKUP FAILS |  |  |
| COMPUTER |  | PASSWORD PROTECTION |  |  |
| RCC COMPUTER |  | CONFIRM FUNCTION IS DUPLICATE OF CONTROL ROOM COMPUTER |  |  |
| + Repeat all tests for Performance Testing |  |  |  |  |  |
| DATE: |  |  |  |  |  |
| TIME: |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |

ITEM 3 - EMERGENCY SHUTDOWN

| EMERGENCY SYSTEM |  |  |  |  |  |  |  |  | EMERGENCY SYSTEM ACTIVATION |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DEVICE LOCATION FOR SHUT DOWN |  |  | LOCATION ID LIGHT ILLUMINATED |  |  | RED PCP ALARM |  |  | EQUIPMENT | VERIFY |  |  |
|  |  |  | YES |  | NO | YES | NO |  |  | ACTION | YES | NO |
| PUMPHOUSE 1 |  |  |  |  |  |  |  |  | FP1 – AUTOMATIC | STOP |  |  |
| PUMPHOUSE 2 |  |  |  |  |  |  |  |  | FP2 – AUTOMATIC | STOP |  |  |
| PUMPHOUSE 3 |  |  |  |  |  |  |  |  | FP3 – AUTOMATIC | STOP |  |  |
| CONTROL RM PCP |  |  |  |  |  |  |  |  | FP4 – AUTOMATIC | STOP |  |  |
| CONTROL RM DOOR |  |  |  |  |  |  |  |  | FP5 – AUTOMATIC | STOP |  |  |
| HHT |  |  |  |  |  |  |  |  | FP1 – MANUAL | STOP |  |  |
| TRUCK FILL STAND 1 |  |  |  |  |  |  |  |  | FP2 – MANUAL | STOP |  |  |
| TRUCK FILL STAND 2 |  |  |  |  |  |  |  |  | FP3 – MANUAL | STOP |  |  |
| TRUCK OFFLOAD 1 |  |  |  |  |  |  |  |  | FP4 – MANUAL | STOP |  |  |
| TRUCK OFFLOAD 2 |  |  |  |  |  |  |  |  | FP5 – MANUAL | STOP |  |  |
| TANK NORTH |  |  |  |  |  |  |  |  | FTP – AUTOMATIC | STOP |  |  |
| TANK SOUTH |  |  |  |  |  |  |  |  | FTP – MANUAL | STOP |  |  |
| TANK EAST |  |  |  |  |  |  |  |  | JP - AUTOMATIC | STOP |  |  |
| TANK WEST |  |  |  |  |  |  |  |  | JP - HAND | STOP |  |  |
| APRON 1 |  |  |  |  |  |  |  |  | OP1 | STOP |  |  |
| APRON 2 |  |  |  |  |  |  |  |  | OP2 | STOP |  |  |
| APRON 3 |  |  |  |  |  |  |  |  | BOWSER PUMP | STOP |  |  |
| APRON 4 |  |  |  |  |  |  |  |  | RP-1 | STOP |  |  |
| APRON 5 |  |  |  |  |  |  |  |  | FSCV – 1 (EMERG SHUTOFF) | SOLENOID DE-ENERGIZED |  |  |
| APRON 6 |  |  |  |  |  |  |  |  | FSCV – 2 (EMERG SHUTOFF) | SOLENOID DE-ENERGIZED |  |  |
| EWS |  |  |  |  |  |  |  |  | FSCV – 3 (EMERG SHUTOFF) | SOLENOID DE-ENERGIZED |  |  |
| FIRE ALARM SYSTEM |  |  |  |  |  |  |  |  | FSCV – 4 (EMERG SHUTOFF) | SOLENOID DE-ENERGIZED |  |  |
| PRT HIGH-HIGH LEVEL ALARM |  |  |  |  |  |  |  |  | FSCV – 5 (EMERG SHUTOFF) | SOLENOID DE-ENERGIZED |  |  |
|  |  |  | + Repeat all tests for Performance Testing |  |  |  |  |  |  |  |  |
|  |  |  | DATE: |  |  |  |  |  |  |  |  |
|  |  |  | TIME: |  |  |  |  |  |  |  |  |
|  |  |  | TEST CONDUCTED BY: |  |  |  |  |  |  |  |  |

ITEM 4 – EMERGENCY EYE WASH AND SHOWER

| ACTIVITY |  | VERIFY | OBSERVED |
| --- | --- | --- | --- |
| EYE WASH FLOW |  | 1.5 GPM |  |
| EYE WASH FLOW |  | TEMPERED WATER (60-100 DEG F) |  |
| EYE WASH FLOW |  | RED PCP ALARM |  |
| SHOWER FLOW |  | 20 GPM |  |
| SHOWER FLOW |  | TEMPERED WATER (60-100 DEG F) |  |
| SHOWER FLOW |  | RED PCP ALARM |  |
| CIRCULATING PUMP |  | FLOW |  |
| + Repeat alarms for Performance Testing |  |  |  |
| DATE: |  |  |  |
| TIME: |  |  |  |
| TEST CONDUCTED BY: |  |  |  |

ITEM 5 – OPERATING TANKS

| OPERATING TANK NO. 1 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| TANK LIQUID LEVEL ELEVATION | PUMP NO. | ACTIVITY |  | YES | NO |
|  |  | HHLA (RED PCP ALARM) AND RECEIPT PUMP SHUT DOWN |  |  |  |
|  |  | HIGH LEVEL VALVE (HLV) CLOSURE |  |  |  |
|  |  | HLA (WHITE PCP ALARM) |  |  |  |
|  |  | LLA (WHITE PCP ALARM) |  |  |  |
|  |  | LLLA (RED PCP ALARM) AND ISSUE PUMP SHUT DOWN |  |  |  |
| NA | NA | LLLA AND RECEIPT VALVE CLOSED (TANK CLEANING) ALARM CLEARS |  |  |  |
| NA | NA | WATER DRAW OFF SYSTEM PUMP ON/OFF |  |  |  |
| + Repeat all tests for Performance Testing Use fuel tank level in the tank for all tests, use exterior manual testing as a last resort. |  |  |  |  |  |
| DATE: |  |  |  |  |  |
| TIME: |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |

ITEM 5 – OPERATING TANKS

| OPERATING TANK NO. 2 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| TANK LIQUID LEVEL ELEVATION | PUMP NO. | ACTIVITY |  | YES | NO |
|  |  | HHLA (RED PCP ALARM) AND RECEIPT PUMP SHUT DOWN |  |  |  |
|  |  | HIGH LEVEL VALVE (HLV) CLOSURE |  |  |  |
|  |  | HLA (WHITE PCP ALARM) |  |  |  |
|  |  | LLA (WHITE PCP ALARM) |  |  |  |
|  |  | LLLA (RED PCP ALARM) AND ISSUE PUMP SHUT DOWN |  |  |  |
| NA | NA | LLLA AND RECEIPT VALVE CLOSED (TANK CLEANING) ALARM CLEARS |  |  |  |
| NA | NA | WATER DRAW OFF SYSTEM PUMP ON/OFF |  |  |  |
| + Repeat all tests for Performance Testing Use fuel tank level in the tank for all tests, use exterior manual testing as a last resort. |  |  |  |  |  |
| DATE: |  |  |  |  |  |
| TIME: |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |

ITEM 6 – FIRE ALARM

| ACTIVITY |  | VERIFY | YES | NO |
| --- | --- | --- | --- | --- |
| PULL STATION |  | ALARM (RED PCP ALARM) |  |  |
| PULL STATION |  | REPORTED TO FIRE DEPARTMENT |  |  |
| SMOKE DETECTOR |  | ALARM (RED PCP ALARM) |  |  |
| SMOKE DETECTOR |  | REPORTED TO FIRE DEPARTMENT |  |  |
| HEAT DETECTOR |  | ALARM (RED PCP ALARM) |  |  |
| HEAT DETECTOR |  | REPORTED TO FIRE DEPARTMENT |  |  |
| + Repeat all tests for Performance Testing |  |  |  |  |
| DATE: |  |  |  |  |
| TIME: |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |

ITEM 7 – PRODUCT RECOVERY TANK

| TANK VOLUME | TANK LIQUID LEVEL ELEVATION |  | ACTIVITY | YES |  | NO |
| --- | --- | --- | --- | --- | --- | --- |
| > 95% |  |  | OV-1 CLOSES (WHITE PCP ALARM) |  |  |  |
| > 90% |  |  | HHLA (RED PCP ALARM) AND EMERGENCY SYSTEM ACTIVATION |  |  |  |
| > 85% |  |  | HLA (WHITE PCP ALARM) |  |  |  |
| > 70% |  |  | PUMP (FTP-1) START |  |  |  |
| < 20% |  |  | PUMP (FTP-1) STOP |  |  |  |
| NA | NA |  | WATER DRAW-OFF PUMP ON/OFF |  |  |  |
| NA | NA |  | RP-1 ON/OFF |  |  |  |
| NA | NA |  | LEAK DETECTION |  |  |  |
| + Repeat all tests for Performance Testing |  |  |  |  |  |  |  |
| DATE: |  |  |  |  |  |  |  |
| TIME: |  |  |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |  |  |

ITEM 8 – FOUR VALVE MANIFOLD

| TANK 1 |  |  |  | TANK 2 |  |  | SELECTOR SWITCH AUTO MODE |  |  | SELECTOR SWITCH TEST MODE |  |  | SELECTOR SWITCH FLUSH MODE |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TANK ISSUE | 4-WAY |  |  | TANK ISSUE | 4-WAY |  |  |  |  |  |  |  |  |  |  |
| VALVE I1 | RETURN VALVE I34 | SYS RECEIPT VALVE R10 |  | VALVE I2 | RETURN VALVE I35 | SYS RECEIPT VALVE R11 | VERIFY | Y | N | Verify | Y | N | Verify | Y | N |
| OPEN | CLOSED | OPEN |  | CLOSED | CLOSED | CLOSED | NO ALARM |  |  | NO ALARM |  |  | NO ALARM |  |  |
| OPEN | CLOSED | OPEN |  | CLOSED | OPEN | CLOSED | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| OPEN | CLOSED | OPEN |  | CLOSED | OPEN | OPEN | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| OPEN | CLOSED | CLOSED |  | CLOSED | OPEN | OPEN | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| OPEN | CLOSED | CLOSED |  | CLOSED | OPEN | CLOSED | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| OPEN | OPEN | CLOSED |  | CLOSED | CLOSED | CLOSED | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| OPEN | OPEN | CLOSED |  | CLOSED | CLOSED | OPEN | NO ALARM |  |  | NO ALARM |  |  | NO ALARM |  |  |
| CLOSED | CLOSED | CLOSED |  | OPEN | CLOSED | OPEN | NO ALARM |  |  | NO ALARM |  |  | NO ALARM |  |  |
| CLOSED | OPEN | CLOSED |  | OPEN | CLOSED | OPEN | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| CLOSED | OPEN | OPEN |  | OPEN | CLOSED | OPEN | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| CLOSED | OPEN | OPEN |  | OPEN | CLOSED | CLOSED | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| CLOSED | OPEN | CLOSED |  | OPEN | CLOSED | CLOSED | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| CLOSED | CLOSED | CLOSED |  | OPEN | OPEN | CLOSED | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| CLOSED | CLOSED | OPEN |  | OPEN | OPEN | CLOSED | NO ALARM |  |  | NO ALARM |  |  | NO ALARM |  |  |
| * |  |  |  |  |  |  | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| * |  |  |  |  |  |  | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| + |  |  |  |  |  |  | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| + |  |  |  |  |  |  | ALARM |  |  | ALARM |  |  | NO ALARM |  |  |
| * Additional random selection of valve position by the System Supplier during Equipment Tests + Repeat three tests (selected by Government Witness) during Performance Testing + Additional random selection of valve positions by the Government Witness during Performance Testing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| DATE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TIME: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

ITEM 9 – TIGHTNESS MONITORING SYSTEM

| SECTION TESTED | PASS/FAIL |  | DURATION (MINUTES) | DETECTED LEAK RATE |
| --- | --- | --- | --- | --- |
| + Initiate test and run for 15 minutes for Performance Testing |  |  |  |  |  |
| DATE: |  |  |  |  |  |
| TIME: |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |

ITEM 10 – FUEL PUMPS

| PUMP NO. | PROPER ROTATION W/PRIMARY POWER |  |  | PROPER ROTATION W/BACKUP POWER |  | SHUT DOWN WITH NO FLOW |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | YES | NO |  | YES | NO | YES | NO |
| FP-1 |  |  |  |  |  |  |  |
| FP-2 |  |  |  |  |  |  |  |
| FP-3 |  |  |  |  |  |  |  |
| FP-4 |  |  |  |  |  |  |  |
| FP-5 |  |  |  |  |  |  |  |
| FTP-1 |  |  |  |  |  |  |  |
| RP-1 |  |  |  |  |  | NA | NA |
| JP |  |  |  |  |  |  |  |
| OP-1 |  |  |  |  |  |  |  |
| OP-2 |  |  |  |  |  |  |  |
| BOWSER PUMP |  |  |  |  |  |  |  |
| + Repeat two tests (selected by Government Witness) for Performance Testing |  |  |  |  |  |  |  |
| DATE: |  |  |  |  |  |  |  |
| TIME: |  |  |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |  |  |

ITEM 11 - FUELING PUMP OPERATION - AUTOMATIC MODE

SELECTED MICROPROCESSOR 	1

SELECTED LEAD PUMP    	    FP-1

XXX-XXX SETPOINT RANGE

{XXX} DEFAULT VALUE

[_____]   CURRENT VALUE

| Measuring Device | Lead Pump Start | Second Pump Start | Third Pump Start | Fourth Pump Start | Fourth Pump Stop | Third Pump Stop | Second Pump Stop | Lead Pump Stop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PIT-1 | 30-150 PSIG {60} PSIG [_____] PSIG |  |  |  |  |  |  | 130-190 PSIG {140} PSIG [_____] PSIG |
| Issue Venturi DPT-1 |  | 450-650 GPM {> 560} GPM [_____] GPM | 1000-1300 GPM {> 1160} GPM [_____] GPM | 1600-1900 GPM {>1760} GPM [_____] GPM |  |  |  |  |
| Return Venturi DPT - 3 |  | 10-100 GPM {< 40} GPM [____] GPM | 10-100 GPM {< 40} GPM [____] GPM | 10-100 GPM {< 40} GPM [____] GPM | 500-800 GPM {> 560} GPM [_____] GPM | 500-800 GPM {> 560} GPM [_____] GPM | 500-800 GPM {> 560} GPM [_____] GPM | 500-800 GPM {> 560} GPM [_____] GPM |
| + Not required for Performance Testing |  |  |  |  |  |  |  |  |
| DATE: |  |  |  |  |  |  |  |  |
| TIME: |  |  |  |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |  |  |  |

ITEM 11 - FUELING PUMP OPERATION - AUTOMATIC MODE

SELECTED MICROPROCESSOR 	1

SELECTED LEAD PUMP  FP- [Contracting Officer Choice]

XXX-XXX SETPOINT RANGE

{XXX} DEFAULT VALUE

[_____]   CURRENT VALUE

| Measuring Device | Lead Pump Start | Second Pump Start | Third Pump Start | Fourth Pump Start | Fourth Pump Stop | Third Pump Stop | Second Pump Stop | Lead Pump Stop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PIT-1 | 30-150 PSIG {60} PSIG [_____] PSIG |  |  |  |  |  |  | 130-190 PSIG {140} PSIG [_____] PSIG |
| Issue Venturi DPT-1 |  | 450-650 GPM {> 560} GPM [_____] GPM | 1000-1300 GPM {> 1160} GPM [_____] GPM | 1600-1900 GPM {>1760} GPM [_____] GPM |  |  |  |  |
| Return Venturi DPT - 3 |  | 10-100 GPM {< 40} GPM [____] GPM | 10-100 GPM {< 40} GPM [____] GPM | 10-100 GPM {< 40} GPM [____] GPM | 500-800 GPM {> 560} GPM [_____] GPM | 500-800 GPM {> 560} GPM [_____] GPM | 500-800 GPM {> 560} GPM [_____] GPM | 500-800 GPM {> 560} GPM [_____] GPM |
| + Repeat during Performance Testing |  |  |  |  |  |  |  |  |
| DATE: |  |  |  |  |  |  |  |  |
| TIME: |  |  |  |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |  |  |  |

ITEM 11 - FUELING PUMP OPERATION - AUTOMATIC MODE

SELECTED MICROPROCESSOR 	2

SELECTED LEAD PUMP  FP- [Contracting Officer Choice]

XXX-XXX SETPOINT RANGE

{XXX} DEFAULT VALUE

[_____]   CURRENT VALUE

| Measuring Device | Lead Pump Start | Second Pump Start | Third Pump Start | Fourth Pump Start | Fourth Pump Stop | Third Pump Stop | Second Pump Stop | Lead Pump Stop |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PIT-1 | 30-150 PSIG {60} PSIG [_____] PSIG |  |  |  |  |  |  | 130-190 PSIG {140} PSIG [_____] PSIG |
| Issue Venturi DPT-1 |  | 450-650 GPM {> 560} GPM [_____] GPM | 1000-1300 GPM {> 1160} GPM [_____] GPM | 1600-1900 GPM {>1760} GPM [_____] GPM |  |  |  |  |
| Return Venturi DPT - 3 |  | 10-100 GPM {< 40} GPM [____] GPM | 10-100 GPM {< 40} GPM [____] GPM | 10-100 GPM {< 40} GPM [____] GPM | 500-800 GPM {> 560} GPM [_____] GPM | 500-800 GPM {> 560} GPM [_____] GPM | 500-800 GPM {> 560} GPM [_____] GPM | 500-800 GPM {> 560} GPM [_____] GPM |
| + Not required for Performance Testing |  |  |  |  |  |  |  |  |
| DATE: |  |  |  |  |  |  |  |  |
| TIME: |  |  |  |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |  |  |  |

ITEM 12 – TRUCK OFFLOAD SKID

| SKID 1 |  |  |  |
| --- | --- | --- | --- |
| ACTIVITY |  | YES | NO |
| Air Eliminator fills completely when truck connects |  |  |  |
| Offload pump is enabled when Low Sensor is exceeded |  |  |  |
| Offload pump is disabled when Scully is disconnected |  |  |  |
| Pump de-energized upon no flow |  |  |  |
| Manual stop will de-energize pump |  |  |  |
| Offload rate begins at 600 gpm |  |  |  |
| Offload slows to 300 gpm when level drops below Upper Sensor |  |  |  |
| Offload rate slows to 150 gpm when level drops below Middle Sensor |  |  |  |
| Offload pump stops when level drops below Low Sensor |  |  |  |
| + Repeat all tests for Performance Testing |  |  |  |  |
| DATE: |  |  |  |  |
| TIME: |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |

ITEM 13 – TRUCK OFFLOAD SKID

| SKID 2 |  |  |  |
| --- | --- | --- | --- |
| ACTIVITY |  | YES | NO |
| Air Eliminator fills completely when truck connects |  |  |  |
| Offload pump is enabled when Low Sensor is exceeded |  |  |  |
| Offload pump is disabled when Scully is disconnected |  |  |  |
| Pump de-energized upon no flow |  |  |  |
| Manual stop will de-energize pump |  |  |  |
| Offload rate begins at 600 gpm |  |  |  |
| Offload slows to 300 gpm when level drops below Upper Sensor |  |  |  |
| Offload rate slows to 150 gpm when level drops below Middle Sensor |  |  |  |
| Offload pump stops when level drops below Low Sensor |  |  |  |
| + Repeat all tests for Performance Testing |  |  |  |  |
| DATE: |  |  |  |  |
| TIME: |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |

ITEM 14 – HYDRANT/TRUCK FILL/HHT CONTROL VALVES

| Hydrant Control Valve (HCV) No. | HCV Size (Inch) | HCV Inlet Pressure (PSIG) | HCV Outlet Pressure (PSIG) | HCV Deadman Closure Rate (SEC) | HCV Max Outlet Pressure During Surge* (PSIG) | HCV Flow Rate (GPM) | Nozzle* Outlet Pressure (PSIG) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nozzle* - Nozzle outlet pressure (skin of the aircraft 45 psi, skin of the truck 35) Surge* (50 psi max aircraft, 40 truck) - Simulate surge by closing truck valve using a 3 second count One pump in operation + All control valves to be witnessed during Performance Testing |  |  |  |  |  |  |  |
| DATE: |  |  |  |  |  |  |  |  |
| TIME: |  |  |  |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |  |  |  |

ITEM 15 - FLUSHING

| FLUSH MODE |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| OPERATING TANK NO. _____ LEVEL-START | OPERATING TANK NO. _____ LEVEL-FINISH |  | PRESSURE GAGE READING AT DEFUEL/FLUSH VALVE (PSIG) | HYDRANT LOOP FLUSH VELOCITY (FPS) | NUMBER OF PUMPS OPERATING |  |
|  |  |  |  |  | 1 |  |
|  |  |  |  |  | 2 |  |
|  |  |  |  |  | 3 |  |
|  |  |  |  |  | 4 |  |
|  |  |  |  |  | 5 |  |
| + Repeat for Performance Testing |  |  |  |  |  |  |
| DATE: |  |  |  |  |  |
| TIME: |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |

ITEM 16 - DEFUELING PERFORMANCE

| AUTOMATIC MODE (WITH ONE OR MORE ISSUE PUMPS IN OPERATION) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| HYDRANT CONTROL VALVE (HCV) NO. | DEFUEL FLOW RATE (GPM) |  | FUELING PUMP NO. |  | FLOW RATE THRU ISSUE VENTURI (GPM) | HYDRANT LOOP ISSUE PRESSURE PIT-1 (PSIG) | FLOW RATE THRU RETURN VENTURI (GPM) |  |
| + Repeat defuel during Performance Testing at one of the hydrant pits as selected by the Government Witness |  |  |  |  |  |  |  |  |
| DATE: |  |  |  |  |  |  |  |
| TIME: |  |  |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |  |  |

ITEM 16 - DEFUELING PERFORMANCE

| FLUSH (DEFUEL) MODE |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| HYDRANT CONTROL VALVE (HCV) NO. | DEFUEL FLOW RATE (GPM) |  |  | HYDRANT LOOP ISSUE PRESSURE PIT-1 (PSIG) | FLOW RATE THRU RETURN VENTURI (GPM) |  |
| + Repeat defuel during Performance Testing at one of the hydrant pits as selected by the Government Witness |  |  |  |  |  |  |
| DATE: |  |  |  |  |  |
| TIME: |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |

ITEM 17 - FILTER SEPARATOR FLOAT CONTROL VALVE MANUAL TEST

| FILTER SEPARATOR | FILTER SEPARATOR CONTROL VALVE WATER SLUG FEATURE OPERATION |  |
| --- | --- | --- |
|  | YES | NO |
| FSI – 1 |  |  |
| FSI – 2 |  |  |
| FSI – 3 |  |  |
| FSI – 4 |  |  |
| FSI – 5 |  |  |
| FSR – 1 |  |  |
| FSR – 2 |  |  |
| + Repeat for Performance Testing |  |  |
| DATE: |  |  |
| TIME: |  |  |
| TEST CONDUCTED BY: |  |  |

ITEM 18 – FUEL SAMPLING RESULTS

| SAMPLING LOCATION | COLOR (PASS/FAIL) |  |  | PARTICULATE (MG/GALLON) | FREE WATER (PPM) |  |
| --- | --- | --- | --- | --- | --- | --- |
| Issue Filter Separator Receipt |  |  |  |  |  |  |
| Pumphouse Return |  |  |  |  |  |  |
| Hydrant Outlet (30% of the outlets) |  |  |  |  |  |  |
| Truck Fill Stand |  |  |  |  |  |  |
| HHT Check Out Station |  |  |  |  |  |  |
| Tank 1 |  |  |  |  |  |  |
| Tank 2 |  |  |  |  |  |  |
| < 2 mg/gallon particulates <10 ppm free water |  |  |  |  |  |  |
|  | QUANTITY (GALLONS) |  |  |  |  |  |
| Contaminated Fuel |  |  |  |  |  |  |
| DATE: |  |  |  |  |  |
| TIME: |  |  |  |  |  |
| TEST CONDUCTED BY: |  |  |  |  |  |

| I certify that the values recorded in Items 1-17 are accurate and correct. (To be signed by System Supplier during Equipment Tests) |  |
| --- | --- |
| DATE: |  |
| SIGNATURE: |  |
| ORGANIZATION: |  |

| I witnessed designated (+) Equipment Tests during Performance Testing. (To be signed by Government Witness(es) during Performance Testing) |  |
| --- | --- |
| DATE: |  |
| SIGNATURE: |  |
| ORGANIZATION: |  |

PERSONNEL PRESENT DURING PERFORMANCE TESTING

| NAME | ORGANIZATION | COMMERCIAL PHONE NO. |
| --- | --- | --- |

REMARKS:

| CLEANING DAY NUMBER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 25 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 |  |  |  |  | 5 |  |  |  |  | 10 |  |  |  |  | 15 |  |  |  |  | 20 |

PRESSURE DROP IN POUNDS PER SQUARE IN (PSI)

CLEANING OPERATION DAILY FLOW VS. PRESSURE DROP GRAPH FOR FILTER SEPARATOR NO. FSI-1

*  ELEMENT CHANGE CRITERIA:   (1)   When pressure drop across filter separator reaches 15 PSI

(2)   When pressure drop is less than previous plot or fails to increase properly

STARTING DATE:   						 		SIGNATURE:

| CLEANING DAY NUMBER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 25 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 |  |  |  |  | 5 |  |  |  |  | 10 |  |  |  |  | 15 |  |  |  |  | 20 |

PRESSURE DROP IN POUNDS PER SQUARE IN (PSI)

CLEANING OPERATION DAILY FLOW VS. PRESSURE DROP GRAPH FOR FILTER SEPARATOR NO. FSI-2

*  ELEMENT CHANGE CRITERIA:   (1)   When pressure drop across filter separator reaches 15 PSI

(2)   When pressure drop is less than previous plot or fails to increase properly

STARTING DATE:   						 		SIGNATURE:

| CLEANING DAY NUMBER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 25 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 |  |  |  |  | 5 |  |  |  |  | 10 |  |  |  |  | 15 |  |  |  |  | 20 |

PRESSURE DROP IN POUNDS PER SQUARE IN (PSI)

CLEANING OPERATION DAILY FLOW VS. PRESSURE DROP GRAPH FOR FILTER SEPARATOR NO. FSI-3

*  ELEMENT CHANGE CRITERIA:   (1)   When pressure drop across filter separator reaches 15 PSI

(2)   When pressure drop is less than previous plot or fails to increase properly

STARTING DATE:   						 		SIGNATURE:

| CLEANING DAY NUMBER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 25 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 |  |  |  |  | 5 |  |  |  |  | 10 |  |  |  |  | 15 |  |  |  |  | 20 |

PRESSURE DROP IN POUNDS PER SQUARE IN (PSI)

CLEANING OPERATION DAILY FLOW VS. PRESSURE DROP GRAPH FOR FILTER SEPARATOR NO. FSI-4

*  ELEMENT CHANGE CRITERIA:   (1)   When pressure drop across filter separator reaches 15 PSI

(2)   When pressure drop is less than previous plot or fails to increase properly

STARTING DATE:   						 		SIGNATURE:

| CLEANING DAY NUMBER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 25 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 |  |  |  |  | 5 |  |  |  |  | 10 |  |  |  |  | 15 |  |  |  |  | 20 |

PRESSURE DROP IN POUNDS PER SQUARE IN (PSI)

CLEANING OPERATION DAILY FLOW VS. PRESSURE DROP GRAPH FOR FILTER SEPARATOR NO. FSI-5

*  ELEMENT CHANGE CRITERIA:   (1)   When pressure drop across filter separator reaches 15 PSI

(2)   When pressure drop is less than previous plot or fails to increase properly

STARTING DATE:   						 		SIGNATURE:

| CLEANING DAY NUMBER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 25 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 |  |  |  |  | 5 |  |  |  |  | 10 |  |  |  |  | 15 |  |  |  |  | 20 |

PRESSURE DROP IN POUNDS PER SQUARE IN (PSI)

CLEANING OPERATION DAILY FLOW VS. PRESSURE DROP GRAPH FOR FILTER SEPARATOR NO. FSR-1

*  ELEMENT CHANGE CRITERIA:   (1)   When pressure drop across filter separator reaches 15 PSI

(2)   When pressure drop is less than previous plot or fails to increase properly

STARTING DATE:   						 		SIGNATURE:

| CLEANING DAY NUMBER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 25 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 |  |  |  |  | 5 |  |  |  |  | 10 |  |  |  |  | 15 |  |  |  |  | 20 |

PRESSURE DROP IN POUNDS PER SQUARE IN (PSI)

CLEANING OPERATION DAILY FLOW VS. PRESSURE DROP GRAPH FOR FILTER SEPARATOR NO. FSR-2

*  ELEMENT CHANGE CRITERIA:   (1)   When pressure drop across filter separator reaches 15 PSI

(2)   When pressure drop is less than previous plot or fails to increase properly

STARTING DATE:   						 		SIGNATURE: