## Facility Life Cycle CPC (1)
Corrosion Prevention and Control (CPC) Checklist Organized by Facility Life Cycle Steps (1)
The CPC Checklists (Checklists 1 – 3), including checklist questions, organization and references) are intended to serve as an assist for facilities professionals (government and contractor) in addressing CPC contract requirements. It is not intended to be complete or apply in every situation (contract, SRM action, RFP). The user must apply good engineering judgement and practice in developing an appropriate checklist that applies to the specific contract and or project (procurement, in-house job). Research into every reference is necessary to ensure compliance with the contract and project. The UFC 1-200-01 DoD Building Code lists Environmental Severity Zones for each DoD location. These Zone designations must be adhered to in developing a design and in selecting appropriate CPC materials and building element corrosion mitigating requirements. Micro-environments will apply in specific areas (swimming pool enclosures, chemical storage, etc.). Note that the "blue" text indicates a hyperlink.
Note that each program/project type will require some, but not necessarily all of the considerations listed below. | Checklist construct: 1. Completed task 2. Not required
Planning & Requirements Definition
Determine Environmental Severity Classification for the project location; if ESC 3 or greater, ensure that CPC is addressed in the project plan
Identify CPC project requirements in accordance with UFC 1-200-01 DoD Building Code
Consult with designated corrosion POC and review CPC requirements and recommendations
Ensure that high-risk corrosion areas been identified and reviewed with the corrosion SME(s)
Include active CPC systems (e.g. cathodic protection) where appropriate
Ensure that CPC imperatives are described in planning and project-document details to ensure resourcing justification during review of project planning documents
Provide CPC insights to the planner as needed
Resourcing & Programming
Establish budget requirements, which include CPC, for project documentation and submission
Depending on the complexity of the CPC portions of the project, ensure that budget includes construction and sustainment requirements (cathodic protection, coatings, etc.)
Provide CPC insights for specific building/component types to the program manager as needed
Engineering & Design
Select CPC criteria requirement level associated with the contract type
Select approved standards and criteria, such as those hosted on wbdg.org, to establish detailed contract performance requirements
Review project specifications/criteria for CPC compliance by the CPC SME
Identify quality assurance (owner/Government) requirements
Include quality control and commissioning requirements in RFP/SOW
Include Environmental Severity Classification (ESC) impacts in the Design – Corrosion Toolbox
Address high sustainment components requirements related to CPC
Select life-cycle-cost-effective material, coatings, active CPC systems and design geometries consistent with the ESC and appropriate to the budget
Consider risk assessment/service life where appropriate
Address technology-integration requirements when editing relevant criteria documents
Modify and edit UFGS criteria appropriate to the required levels of CPC requirements
Ensure that engineering and design professionals stay current on CPC technologies and processes. See CPC Source and the WBDG for more information
Construction & Commissioning
Include discussion of CPC requirements in design-kickoff discussion
Identify the CPC inspection schedule to ensure that it is no less frequently than mandated by specific service and develop the survey template using minimum requirements as a guide
Ensure that CPC is considered and survives design modifications and construction deviations
Delineate and execute oversight requirements in QA, QC, Commissioning (Cx) processes
Ensure that personnel overseeing quality are trained in CPC aspects of the project and are qualified to assess quality and constructed requirements consistent with contract
Resist tradeoffs that result in elimination of CPC project requirements and quality levels
Document CPC features in as-built drawings & project data (eOMSI)
Conduct CPC-specific operator training
Ensure that facility turnover includes discussion along with documentation transfer of CPC features
Ensure that construction personnel are current on CPC technologies and processes. See CPC Source and the WBDG
Sustainment, Restoration, & Modernization
Develop CPC preventive-maintenance strategy and program
Identify the funding required for post-construction sustainment efforts and the program to ensure proper condition survey actions and maintenance activities
Conduct CPC inspections. Record data related to type and extent of corrosion, component materials, coatings, warranty applicability, age, maintenance history, and effectiveness of cathodic protection systems into SMS
Conduct regular inspections that include focused CPC evaluations and recommendations
Follow best-practice CPC maintenance planning and work scheduling
Ensure that management understands and supports CPC Sustainment requirements
Ensure that the management of CPC sustainment supports the operations and mission of the organization
If installation resource board has approval authority over projects, ensure that CPC expert provides insights to facilitate prioritization and timely execution
Ensure that SRM professionals are current on CPC technologies and processes. See CPC Source and the WBDG for more information
Demolition & Disposal
Review and follow applicable criteria and local guidance. Criteria include: UFGS 02 41 00 [Demolition] [and] [Deconstruction], UFGS 01 74 19 Construction Waste Management and Disposal
Consult with appropriate hazardous-materials specialist
Inspect facility for corrosion-related deterioration causing unsafe conditions during demolition process
Assess presence of hazardous materials
Dispose of materials in approved manner
Acquisition Issues in Support of the FLC
Select contract type most appropriate to available budget, risk and project expectations
Develop project plan, budget and documentation
Ensure technical review includes CPC requirements for contractor's proposal
Include discussion of CPC requirements in design kickoff discussion
Ensure that construction personnel are current on CPC technologies and processes. See CPC Source and the WBDG for more information. See also CPC Source – Acquisition Issues and the D, CPO Recommended Facilities Corrosion Training Summary Track 7 – Acquisition Professional for additional information

## Facility CPC Program MGT (2)
Corrosion Prevention and Control (CPC) Checklist Organized by Facility Program Management Categories (2)
The following Focus Areas and the Questions with the associated evaluation have their roots in the "ARMS" Guide (ARMS Guide: Maintenance and Aviation Support Equipment Operations) and the Air Force Corrosion Assessment Program. Facilities are not the focus of the ARMS Guide document; however, the following construct is based upon the ARMS Guide contract and program evaluation approach. The Air Force (AF) CPC Program Assessment Guide is focused on facilities. Of course, the objective of this construct is to assist with the assessment and effectiveness of the CPC program (both government and contract). The areas of CPC organization (such as program and project management, safety, competencies, sustainment management system (SMS), quality management) are the focus of this checklist. It includes areas of evaluation that should be addressed for both a contractor or government program (in-house). Any evaluation factors and weighing should be established for each contract or program. Any grading shown here is notional. The user should adapt the entries to the specific contract or in-house CPC program to be evaluated and monitored. Note that while several questions imply that the "contractor" is performing the work or function, but it is possible that government forces could be doing the work or function as well.
The CPC Checklists (Checklists 1 – 3), including checklist questions, organization and references) are intended to serve as an assist for facilities professionals (government and contractor) in addressing CPC contract requirements. It is not intended to be complete or apply in every situation (contract, SRM action, RFP). The user must apply good engineering judgement and practice in developing an appropriate checklist that applies to the specific contract and or project (procurement, in-house job). Research into every reference is necessary to ensure compliance with the contract and project. The UFC 1-200-01 DoD Building Code lists Environmental Severity Zones for each DoD location. These Zone designations must be adhered to in developing a design and in selecting appropriate CPC materials and building element corrosion mitigating requirements. Micro-environments will apply in specific areas (swimming pool enclosures, chemical storage, etc.).
Focus Area & Questions | Government Contract Development Checklist and Evaluation Contract Request for Proposal (RFP) 1. Are the relevant line items below addressed in the RFP; 2. Does the Government have an oversight plan to monitor and approve the contractor's execution of the relevant line items included in the contract? | Contractor Evaluation Did the Contractor include the relevant line items in their design, construction and quality assurance plan? Select appropriate grading words such as "1. Meets contract requirements; 2. Fails to meet contract requirements; or, 3. Improvements in the following (select) areas are required" | Contractor Evaluation Did the Contractor Execute the Relevant Line Items Select appropriate grading words such as "1. Meets contract requirements; 2. Fails to meet contract requirements; or, 3. Improvements in the following (select) areas are required") | Assigned Points if Applicable Include an evaluation based upon contract or organizational evaluation plan established grading criteria delineated in the contract. | References Note that the references provided are not intended to be a complete or absolute list. Each user should add their own references as needed.
Contract Requirements
Does the Contract RFP describe CPC roles and responsibilities (R&R)?
Have those R&R been summarized in the operating procedure and contract document?
Does the contract require that the contractor have a CPC Program in place?
Does the contract require periodic CPC reporting and assessment?
Is the CPC reporting broken down by facility category, location, building number, system, etc.? (LS comments: We should be more specific than "etc.")
Does the reporting system include recommended actions?
Does the contractor have access to relevant guidance (such as for components, installation, and SOPs)?
Are submittals and plans identified in the RFP and contract?
Are the qualifications and certifications identified in the contract? For example, if Cathodic Protection is required, has a Registered PE supervised the electrical service design IAW UFC 3-570-01? |  |  |  |  | UFC 3-570-01 Cathodic Protection; UFC 3-570-06 O&M: Cathodic Protection Systems
Has CPC expertise been identified to ensure that the project has appropriate input at the pre-design and construction stages? Who will be in charge of ensuring CPC requirements have been met? |  |  |  |  | AR 420-1 Facilities Engineering: Army Facilities Management
Does the local project POC know and have access to (Army, Navy, Air Force) corrosion expertise if needed? |  |  |  |  | AR 420-1 Facilities Engineering: Army Facilities Management
Are functional test and evaluation procedures identified and in place for the CPC program?
Request for Proposal/Statement of Work (RFP)/(SOW)
Does the RFP/SOW delineate specific criteria requirements from the WBDG (https://www.wbdg.org/ffc/dod)?
Is the performance plan keyed to specific sections of those criteria (especially UFC and UFGS)?
Are the CPC requirements in the criteria reflected in the RFP/SOW?
Have UFC 1-200-01 and the applicable ESC Zone requirements been identified, including specific material types (paints, coatings, steel, etc.)?
Have the ESC factors been applied to the design?
Have UFCs 1-200-01, 1-300-01, and 1-300-02 been followed? |  |  |  |  | UFC 1-200-01 DoD Building Code, UFC 3-101-01 Structural Engineering, UFC 1-300-02 Unified Facilities Guide Specifications (UFGS) Format Standard
Has CPC SME assistance been provided to the design/construction team? Have CPC technologies been considered to improve life cycle performance? |  |  |  |  | AR 420-1 Facilities Engineering: Army Facilities Management
Have project specifications and criteria been reviewed for CPC compliance by the CPC SME? |  |  |  |  | AR 420-1 Facilities Engineering: Army Facilities Management
Has the Project CPC SME reviewed and approved paints, coatings, cathodic protection, material selection, and other CPC requirements and submittals in the contract requirements and associated design? |  |  |  |  | AR 420-1 Facilities Engineering: Army Facilities Management
Quality Evaluation
Is there a formal CPC Plan delineating R&R? Is this plan keyed to contract requirements including design, construction and sustainment actions?
Do the Commissioning (Cx) reports include enough detail related to CPC? Are those reports consistent with the eOMSI UFGS 01 78 24.00 20 (https://www.wbdg.org/FFC/NAVFAC/NDBM/UFGS/01_78_24.00_20.pdf)? |  |  |  |  | UFGS 01 78 24.00 20 Facility Electronic Operation And Maintenance Support Information (EOMSI)
Does the Contract define the type of CQC Program and associated detail/construct to include referencing appropriate FAR and DFARS clauses? Does the CQC Program achieve contract goals? Is it effective? What reports are provided to the government? What is the approach for corrective actions?
Quality Assurance (QA) (Gov't)
Does the Government have an established CPC QA program?
Has the CPC QA program been tailored for the current contract or government workforce project?
Are the Government QA personnel trained to assess CPC project work phases?
Does the current contract acknowledge Government CPC QA plans, and is it linked to the contractor's workplan? |  |  |  |  | FAR Clause 52.236-5 Material and Workmanship. Material and Workmanship (Apr 1984); Clause 52.246-12 Inspection of Construction (Aug 1996)
Has the contractor refrained from substituting a material that has less corrosion resistance than required?
Has the contractor used good design and construction practice, including incorporating CPC requirements?
Has the contractor identified the ESC Zone for the project location and provided a design that is consistent with that ESC zone's CPC risks and UFC/UFGS requirements?
Has the contractor allowed for good SRM practices for the post-project turnover period? In other words, has the contractor incorporated good design and construction practice into the life-cycle considerations required in the project?
Has the contractor followed good construction and storage practice to minimize materials damage prior to utilizing the materials?
Quality Control (QC) (Ctr)
Does the contractor have a CPC “Contractor Quality Control” (CQC) Program? The contract should define the type of CQC Program and associated detail/construct. |  |  |  |  | FAR Clause 52.236-5 Material and Workmanship. Material and Workmanship (Apr 1984); Clause 52.246-12 Inspection of Construction (Aug 1996)
How detailed/complete is the program? Does it include testing? Feedback loop? Failure analysis? Is it supported by the contractor? To whom does the CQC representative report? |  |  |  |  | FAR Clause 52.236-5 Material and Workmanship. Material and Workmanship (Apr 1984); Clause 52.246-12 Inspection of Construction (Aug 1996)
Does the CQC Program achieve contract goals? Is it effective? What reports are provided to the Government? |  |  |  |  | FAR Clause 52.236-5 Material and Workmanship. Material and Workmanship (Apr 1984); Clause 52.246-12 Inspection of Construction (Aug 1996)
What is the approach for corrective actions? |  |  |  |  | FAR Clause 52.236-5 Material and Workmanship. Material and Workmanship (Apr 1984); Clause 52.246-12 Inspection of Construction (Aug 1996)
Commissioning (Cx) (Ctr)
Does the contractor have a Commissioning (Cx) Program and written plan that includes CPC requirements? Does the contractor have a CPC SME, and has that SME reviewed all corrosion requirements and established an associated CPC commissioning plan?
How detailed/complete is the program? Does it include testing? Feedback loop? Failure analysis? Is it supported by the Contractor? Who does the CQC representative report to?
What links are there to the Government QA program for this project?
What are the reporting requirements? What level of detail is required, and does it address CPC?
SAFETY
Does the contractor have an approved safety plan or safety program?
Are topics such as site preparation, breathing protection, arc-flash protection, and confined-space protection included, as appropriate, for installing and maintaining paints, coatings, and cathodic protection?
Is there an established approval process for this plan to include coordination with the Government and the contractor personnel actually doing the work?
Are there hazardous materials planned for use in executing the CPC project (preservatives, hexavalent chromium, paints and coatings)? Does the safety plan address the handling and use of these materials?
CPC Program
Are CPC Responsibilities clearly defined in a written CPC Plan? CPC inspection schedule? CPC data collection and reporting? CPC materials storage and care program?
How effective is the MOP and associated execution? Does the MOP state required qualifications for personnel? Are personnel qualified for the work they will perform? Is the required CPC training provided?
Are materials protected during storage? How well is corrosion avoided on materials while they are in storage?
Has the funding required for post-construction sustainment efforts been identified and programmed to ensure proper condition survey actions and maintenance activities?
Is the CPC Program coordinated with the contractor's CQC and Cx programs?
RESPONSIBILITIES
Is there a CPC management operating instruction or contractor procedure published? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems
Does the contractor or installation have a quarterly Corrosion Control Committee meeting? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems
Has a process to review and evaluate corrosion planning for new construction and Sustainment, Restoration, and Modernization (SRM) projects been established? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems
Are designs, design reviews and construction inspections accomplished by qualified individuals? Does the CPC plan identify these qualifications? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems
Does the contractor or installation maintain and provide a listing of individuals assigned to the contract with corrosion qualifications? Are those qualifications synched with the appropriate UFC/UFGS criteria and additional contract requirements?
Is appropriate training for maintenance personnel on corrosion control systems identified and scheduled, if needed? Is that training identified in the Cx plan?
PROJECTS
Are corrosion control requirements properly planned and programmed as projects and reviewed and inspected by qualified individuals? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
Are the detailed project checklist actions listed by facility category included in the CPC Plan and Program?
Are corrosion control functional requirements incorporated into material selection, design and construction for projects? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
Has the appropriate CPC engineer been assigned by appointment letter? Have the position and associated roles and responsibilities been included in the contract? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems; AR 420-1
Have cathodic protection, protective coatings, industrial water treatment (IWT) and design/material selection technicians/engineers been assigned by appointment letter? Are these roles identified in the contract? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems
Are these requirements reflected in the CQC, QA and Cx plans?
(For the Air Force) Has a Base Corrosion Control Engineer (BCCE) been assigned by appointment letter?
(For other services) Has a Organizational Corrosion Control Engineer been assigned by appointment letter? |  |  |  |  | AR 420-1 Facilities Engineering: Army Facilities Management
TRAINING- Personnel Qualifications and Training (See CPC Source Training Page and Recommended Training Table (https://www.wbdg.org/ffc/dod/cpc-source/training) and CPC Source Competencies (https://www.wbdg.org/ffc/dod/cpc-source/competencies) for insights as well as specific guidance in applicable UFC and UFGS.
Has the Corrosion Engineer attended or been scheduled for annual training? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; AR 420-1 Facilities Engineering: Army Facilities Management
Are appropriate qualifications and training identified in the RFP and CPC Plan?
Are CP personnel appropriately qualified and trained? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; AR 420-1 Facilities Engineering: Army Facilities Management
Is specialized training for protective coatings, Industrial Water Treatment (IWT), and design/material selection personnel documented as Squadron or Organizational Operating Instruction specifies? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; AR 420-1 Facilities Engineering: Army Facilities Management
Do projects include appropriate training for maintenance personnel on corrosion control systems? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems
RECORDKEEPING AND DOCUMENTATION
Submittals and Plans: Preconstruction - Qualifications of Installer, Shop Drawings, Data Sheets, and Calculations
Submittals and Plans: Preconstruction - QC Plan
Submittals and Plans: Preconstruction - Performance Verification Plan
Certificates and Reports: Construction - Functional Acceptance Test Procedure
Certificates and Reports: Construction - Preliminary Test Reports
Certificates and Reports: Construction - Final Acceptance Test Reports
Are all appropriate data being recorded for galvanic/sacrificial-anode systems consistent with CPC references (example the CP Rectifier Report in UFC 3-570-06)? |  |  |  |  | For Air Force see AF Information Management Tool (IMT) 1686; AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems
Are all appropriate data being recorded for impressed current systems consistent with CPC references (example the CP Rectifier Report in UFC 3-570-06)? |  |  |  |  | For Air Force see AF IMT 491; AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems
Are there base maps showing CP systems, test points and utility locations? |  |  |  |  | Not required per AFI, but are helpful in CP work; UFC 3-570-06 O&M: Cathodic Protection Systems
Are data records for leaks and failures being filled out? |  |  |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems; Document AF IMT 1687
Are records for protective coatings maintained? |  |  |  |  | UFC 3-190-06 Protective Coatings and Paints and AFI 32-1054 Civil Engineer: Corrosion Control
Are these and other data and records included in the CQC, Cx and eOMSI submittals? |  |  |  |  | UFGS 01 78 24.00 20 FACILITY ELECTRONIC OPERATION AND MAINTENANCE SUPPORT INFORMATION (eOMSI)
Is there a CPC Inspection Plan that is being followed? Are records (inspection reports, catalog cuts, job order creation and tracking, etc.) recorded and accessible?
Maintenance Management, Facility Data related to CPC and SMS
Are the Sustainment Management System (SMS) applications such as BUILDER/PAVER/FUELER utilized?
Does the contractor have a maintenance management program that identifies CPC issues?
How accurate is the contractor’s program? Does it identify routine maintenance requirements? Are they scheduled and effectively accomplished?
Is there an established maintenance management program that includes CPC? |  |  |  |  | AR 420-1 Facilities Engineering: Army Facilities Management
Is there a planned/preventative maintenance program? Are records kept showing details to the CPC level, to include details of SRM, dates of actions? |  |  |  |  | AR 420-1 Facilities Engineering: Army Facilities Management
Are CPC inspection and testing records maintained, including the personnel performing inspections, their qualifications, inspection results, and recommendations for follow-up actions?
Are the results of the PM program reflected in project descriptions when justifying project work?
Have the CPC requirements for building systems (CP, paints/coatings, inspections, steel selection, door and window types, design geometries) been identified as high risk to corrosion and the life cycle been flagged in SMS to ensure they are monitored at the appropriate levels? Has the associated corrosion maintenance been entered into SMS along with other condition reports?
Are the data discovered during SRM activities being recorded into the SMS?
Are the data recorded in a Maintenance Management System (MMS)?
How are the data generated from the above listed questions recorded and leveraged in maintenance management systems?
Abbreviations and References
Abbreviations | MAIN REFERENCES
CP - Cathodic Protection | UFC 3-570-01, Cathodic Protection, Nov 2016
OI – Operating Instruction | UFC 3-570-06, Operations and Maintenance: Cathodic Protection Systems, Dated 31 January 2003
EWT – Elevated Water Tank | AFI 32-1054, Corrosion Control, Nov 2014
FAR - Federal Acquisition Regulations | Various
FP – Fire Protection (Tank) | UFC 3-190-06, Protective Coatings and Paints
IWT – Industrial Water Treatment | UFC 3-240-13FN, Industrial Water Treatment Operation and Maintenance
MFH – Military Family Housing | AFI 32-1067, Water and Fuel Systems; AR 420-1 Facilities Engineering: Army Facilities Management

## Organized by Facility Type (3)
Corrosion Prevention and Control (CPC) Checklist Organized by Facility System (3)
General
1. A facility is defined as a real property entity consisting of one or more of the following: a building, a structure, a utility system, pavement, and underlying land (in accordance with JP 3-34). Facilities include buildings, structures, airfields, port facilities, surface and subterranean utility systems, heating and cooling systems, fuel tanks, pavements, and bridges. They include both vertical (buildings, bridges, etc.) and horizontal (roads, utility systems, etc.) structures. The term "facilities" includes infrastructure and structures described in this paragraph.
2. Environmental severity is defined as the corrosivity of the local environment of a given location or region. Environmental severity contributes directly to the occurrence and rate of corrosion. The effects of corrosion and the rate at which they occur are consequences of the corrosion system, which is comprised of a material or physical system, the environment, and operational conditions. Recent changes to UFC 1-200-01 DoD Building Code and several UFCs and UFGSs require ESC evaluations and considerations in the design of facilities. These evaluations and considerations should help in the planning, RFP development and design justification for more CPC-resistant designs in ESC Zones C3 through C5.
3. The ISO Corrosivity Classification method is contained in ISO 9223:2012. This method consists of corrosivity categories defined by first-year corrosion effects on standard specimens as specified in ISO 9226. ISO Corrosivity Categories can be assessed in terms of the most significant atmospheric factors that influence the corrosion of metals and alloys. In this sense, ISO Corrosivity Categories characterize the corrosivity of the atmospheric environment and can provide a basis for the selection of materials and systems that are subject to the demands of the specific application and its required service life. (See UFC 1-200-01)
4. Factors contributing to corrosion include: Atmospheric corrosion factors (temperature, time of wetness [TOW], atmospheric contaminants, solar radiation); abrasive stresses such as erosion from wind due to presence of particulates such as sand; abrasive stresses in water from solid debris or flow/current affecting waterfront and/or immersed structures and components; salinity and associated negative impacts due to areas where deicing salt is used; in areas where condensation may occur at regular intervals such as in cooling pipes and contributes to surface wetness; stresses on structural materials or components due to strain, compression, elasticity, tensile forces, repetitive actions, etc. and/or high temperatures causing stress corrosion cracking; corrosive soils; applied chemicals and contaminants (including pesticides), immersed corrosion factors (soil water); increased presence of corrosive atmospheric contaminants due to facility type/use (i.e. pollutants derived from a facility generating pollutants); biological (insects, bacteria, and fungi [mold and mildew]); internal environments (pipelines and tanks); erosive forces (wind, rain, wave action, fluid flow)
5. The actual environment that affects a specific material or system correlates directly to the conditions of its micro-environment (the local environment that occurs on the surface of the material or system), which can vary even over small distances. Micro-environments with differing environmental severity can occur within a given environment or zone. a. In heating, ventilation, and air conditioning (HVAC systems), temperature differentials of air, liquid, or gas in ductwork or conduits, and surrounding environment can accelerate corrosion. In areas of high humidity or industrial pollutants, the HVAC system must be designed to address the micro-environment impacts on the facility. b. The cost of management and associated impacts of the micro-environment are generally high and are a significant cost of the total project. c. Addressing micro-environment impacts and corrosion in general in initial estimates, along with high-level documentation in the DD Form 1391 Fiscal Year XX Military Construction Project Data, will ensure that the system and components are adequately funded and constructed once approved.
6. The UFC 1-200-01 Building Code is the primary UFC and must be utilized in guiding the planning, design and construction of projects. Relevant UFGS sections reference UFC 1-200-01 and provide greater technical details to be addressed in contract specifications (see https://www.wbdg.org/ffc/dod). The criteria listed below apply to this section on doors, exterior closures and hardware. This is a general listing of criteria related to this section and not necessarily specific to the questions asked in the adjacent columns.
7. The CPC Checklists (Checklists 1 – 3), including checklist questions, organization and references) are intended to serve as an assist for facilities professionals (government and contractor) in addressing CPC contract requirements. It is not intended to be complete or apply in every situation (contract, SRM action, RFP). The user must apply good engineering judgement and practice in developing an appropriate checklist that applies to the specific contract and or project (procurement, in-house job). Research into every reference is necessary to ensure compliance with the contract and project. The UFC 1-200-01 DoD Building Code lists Environmental Severity Zones for each DoD location. These Zone designations must be adhered to in developing a design and in selecting appropriate CPC materials and building element corrosion mitigating requirements. Micro-environments will apply in specific areas (swimming pool enclosures, chemical storage, etc.).
Facility System | CPC Focused Question or Action Related to the Facility System | Government Evaluation of the Request for Proposal and or Design: Are the Relevant Line items Addressed in the RFP? | Contractor Evaluation Did the Contractor include the relevant line items in their design, construction and quality assurance plan? Select appropriate grading words such as "1. Meets contract requirements; 2. Fails to meet contract requirements; or, 3. Improvements in the following (select) areas are required" | Reference UFC, UFGS, OSD, MILDEP Guidance & Policy Cites (Not intended to be a complete listing)
Building Enclosure - Exterior Construction
| In a highly corrosive environment, exterior equipment and system failure (e.g. roof, windows, doors), rust, mildew, weather effects and related corrosion risks must be considered and addressed in the design, construction and sustainment. |  |  | UFC 1-200-01 DoD Building Code, UFC 3-101-01 Architecture, UFC 3-190-06, Protective Coatings and Paints, UFC 3-201-01 Civil Engineering, UFC 3-220-01 Geotechnical Engineering
Have humidity, rain, wind, temperature, moisture, corrosive chemical reactions, efflorescence, abrasion, pitting, dissimilar metals causing galvanic corrosion, mold, mildew, and airborne corrosive pollutants been addressed in the design and sustainment?
Have the operational impacts of Corrosion, Prevention and Control been factored into structural integrity, morale, safety, high sustainment cost impacts, and reduced life cycle considerations? Have those CPC impacts been factored into the planning, design, construction and sustainment?
Doors, Exterior Closures, & Hardware
In highly corrosive environments, poor performing doors (including weather stripping, etc.) increase exposure of equipment and building interior risking component system failure and increase the appearance of rust, mildew, weather affects and related corrosion risks. Have these risks been factored into the design?
Humidity, rain, chloride-containing environments, structural loading, airborne and applied chemicals and contaminants, erosive forces, and incompatible materials create a hostile environment for doors. Have these risks been factored into the design, construction and sustainment?
Doors are one of the most important building envelope barriers to the elements; repetitive use causes deterioration in hardware and weather-stripping, allowing water and wind intrusion, in turn resulting in barrier efficiency and effectiveness. Have these risks been factored into the design, construction and sustainment?
Does the design: | 1. Incorporate good design geometrics that eliminate or discourage corrosion? 2. Account for and mitigate corrosion risks indicated by the applicable ESC Zone? 3. Ensure that the design component or assembly complies with the requirements from the RFP, including technical performance specifications and referenced UFC and UFGS documents? 4. Have drawings and specifications that address CPC through a proper choice of materials and coatings? 5. Avoid poorly-performing materials and coatings that may be motivated only by low up-front costs? |  |  | UFC 3-101-01 Architecture, UFC 3-190-06 Protective Coatings and Paints, UFC 3-301-01 Structural Engineering, UFC 4-211-01 Aircraft Maintenance Hangars, UFC 4-440-01 Warehouse and Storage Facilities, UFC 4-010-01 DoD Minimum Antiterrorism Standards for Buildings, with Change 1 UFC 4-010-03 Security Engineering: Physical Security Measures For High-Risk Personnel UFC 4-020-01 DoD Security Engineering Planning Manual UFC 4-141-10N Design, Aviation Operation and Support Facilities
Does the Design: | 1. Select and specify door-related materials and coatings that have low life-cycle costs, are durable, and minimize the need for preventative and corrective maintenance? (Note that initial investments in corrosion prevention are typically more LCC-effective than the maintenance, repair, and replacement of prematurely degraded components.) 2. Design and specify doors and associated components to reach the intended service life, including the use of enhanced materials and coatings in severe corrosive environments? |  |  | UFGS 08 11 16 Aluminum Doors and Frames; UFGS 08 11 69 Metal Storm Doors; UFGS 08 11 73 Sliding Fire Doors; UFGS 08 13 73 Sliding Metal Doors; UFGS 08 32 13 Aluminum Sliding Glass Doors; UFGS 08 33 13 Metal Rolling Counter Doors; UFGS 08 33 23 Overhead Coiling Doors; UFGS 08 34 16 Corrosion Control Hangar Doors; UFGS 08 34 16.10 Steel Sliding Hangar Doors; UFGS 08 34 19.10 20 Rolling Service [And Fire] Doors;
Does the Design: | Consider the appropriate ESC Zone, deicing salts, pollution, chemicals (caustic and sterile locations), door function, wind load criteria, high-performance building requirements, and door locations (loading docks, warehousing, hangars, etc.)? |  |  | UFGS 08 34 63 Detention Hollow Metal Frames, Doors, and Door Frames; UFGS 08 36 13 Sectional Overhead Doors; UFGS 08 36 19 Vertical Lift Doors; UFGS 08 39 53 Blast Resistant Doors (Oval Arch Magazines); UFGS 08 39 54 Blast Resistant Doors; UFGS 08 71 00 Door Hardware; UFGS 08 91 00 Metal Louvers; UFGS 09 90 00 Paints and Coatings; UFGS 09 96 00 High Performance Coatings; UFGS 09 97 13.00 40 Steel Coatings; UFGS 09 97 13.27 Exterior Coating of Steel Structures
Does the design address: | 1. Selection of the correct coatings, appropriate applications, or correction of damages that occur during construction? 2. Allowance for interior or bathroom door issues to mitigate general corrosion and hinge corrosion? 3. Corrosion factors that are in proximity to saltwater, rainfall, temperature, humidity, and UV exposure, and specify doors that eliminate the use of carbon steel fasteners, hinges, and general components? (Note that if carbon steel is used in construction, the design must specify the proper corrosion control coatings.) 4. Conditions that cause entrapment of water and moisture entrapment, locations of doors and surrounding area impacts? 5. Door finishes that comply with both design appearance and ESC Zone requirements? 6. Avoidance of incompatible materials and dissimilar metals?
Does the design accomplish the following: | 1. Eliminating or limiting the source of water to resist corrosion? 2. Civil design criteria, to require a minimum 2-foot overhang beyond exterior walls? (Note that this practice aids in keeping the water away from the building envelope and therefore decreases water intrusion.) 3. Using SS fasteners to replace carbon steel fasteners? 4. Review and coordination by a committee of public works, design and maintenance, safety, environmental, and security personnel to ensure the project is fully coordinated before release? |  |  | Note that while Guam and the associated MDACS requirements are the focus of several of the following entries, it is instructive to see how that area has addressed ESC 4 and 5 corrosion requirements. The user of these checklists should develop their own checklist entry for the respective ESC, structure, building element, and use type.
For tropical locations (MDACS), have the following been implemented? | 1. "All hardware [and fasteners] shall be 316L stainless steel. If 316L is not available as either standard or as a custom option, then the next highest corrosion resistant stainless steel shall be used" 2. "All exterior doors shall have seal and door bottom to prevent wind driven rain from entering" 3. "Address the requirement that all exterior door hardware shall be designed meet the requirements for Guam's typhoon winds, wind driven rains, wind borne flying debris, wind topographic effect, corrosion and seismic loads as per UFC and ASCE 7 criteria and sections Wind, Seismic, and Corrosion" |  |  | Marianas Navy and Marine Corps Design and Construction Standards (September 2017); UFC 1-200-01 DoD Building Code. Guam is classified as ESC Zone C-5 (coastline) or C-4 (inland).
For tropical locations (MDACS), has the following been implemented? | For tropical locations (MDACS) does the design/project comply with the Doors Section in MDACS? Does it comply with the ESC requirements in UFC 1-200-01 Building Code and UFC 3-101-01 Architecture? The MDACS requires that all exterior doors and frames shall be aluminum with anodized finish (at all facilities except residential) and fiberglass doors with simulated wood finish (single family residential only) or galvanized painted steel interior garage fire doors / frames that swing out into the garage where fire resistive requirements dictate? All exterior doors shall meet the wind, seismic and corrosion requirements. Ensure that the door and window composition and finish are consistent with the ESC Zone requirements and the base exterior architecture plan. |  |  | Marianas Navy and Marine Corps Design and Construction Standards (September 2017); See UFC 1-200-01 DoD Building Code and UFC 3-101-01 Architecture. Guam is classified as ESC Zone C-5 (coastline) or C-4 (inland).
For MDACS Door Hardware, does the design meet the following requirements? | "1. All exterior and interior door hardware, fasteners, etc. shall be 316L unless not available by special order, then order the next highest corrosive stainless steel available and as last choice, hot dipped galvanized with factory painted high corrosive resistant coatings. 2. Hardware shall include threshold, door bottom, and weather seal. 3. All exterior doors shall have concrete step detail that prevents water from being driven directly under door sills and thresholds, and comply with accessibility. 4. Exterior doors and garage doors shall have weather seals and automatic door bottoms (swing doors) to prevent wind-driven rain from entering facility spaces" |  |  | Marianas Navy and Marine Corps Design and Construction Standards MDACS) (September 2017); See UFC 1-200-01 DoD Building Code. Guam is classified as ESC Zone C-5 (coastline) or C-4 (inland).
For Tropical Locations (MDACS, Section 5.2.3.4): | 1. Do exterior doors meet the following minimum requirements: "Main entrances: Medium stile, full glazed aluminum door with aluminum frame. Provide pair of doors at major facilities and where required? 2. For Side entrances: Flush aluminum door; and provide side-lite/vision panel where required? 3. For Utility and other exterior doors: Flush aluminum door. Provide pair of doors only where required? (Note that unless otherwise noted in the project requirements, all exterior doors shall be 3'x7'. Note that exterior doors shall be protected with sun/rain shade/overhang. Note that it is required that storefronts and doors with glazing are protected with typhoon shutters.)" |  |  | Marianas Navy and Marine Corps Design and Construction Standards (MDACS) (September 2017); See UFC 1-200-01 DoD Building Code. Guam is classified as ESC Zone C-5 (coastline) or C-4 (inland).
For Tropical Locations (MDACS): | 1. Does the glazing requirement at exterior door openings meet IBC and ASCE 7 requirements (latest adopted editions at time of project award), and are vision panels eliminated in exterior doors unless required by code or UFC criteria? 2. Are exterior doors with typhoon-rated vision panels that exceed 100 in2 in area provided with typhoon-rated shutters? 3. Are exterior swing doors designed to swing out to allow frame rabbet to act as a stop to prevent door from blowing in and having door seals compress by door against door frame side and to rabbets? 4. Do doors have handicap rated weather sealed thresholds and automatic door bottoms or door shoe with drip? 5. Does the door threshold have concrete recessed seat and 316L stainless steel door sill pan flashing with end dams, rear leg and turned-down front leg? 6. Does the top of door have 316L stainless steel (or most corrosive resistant stainless steel available) drip with hook at top of exterior door frame? |  |  | Marianas Navy and Marine Corps Design and Construction Standards (MDACS) (September 2017); See UFC 1-200-01 DoD Building Code. Guam is classified as ESC Zone C-5 (coastline) or C-4 (inland). See comment in line 24 above and in line 26 above column b.
Hangar Doors | 1. Have the requirements in criteria been addressed in the design? 2. Is the selection of coatings consistent with the ESC Zone for the area of construction? 3. Are areas protected from corrosion including controls, rails, sills, and hardware? 4. Have the appropriate steel and coating been selected? |  |  | UFC 4-211-01 Aircraft Maintenance Hangars; UFC 4-211-01N Aircraft Maintenance Hangars Type I, Type II and Type III; UFGS 08 34 16 Corrosion Control Hangar Doors; UFGS 08 34 16.10 Steel Sliding Hangar Doors; UFGS 09 90 00 Paints and Coatings; UFGS 09 96 00 High-Performance Coatings
Has the installation been periodically rinsing doors and hardware in a salt-laden environment, either through rainwater exposure or a maintenance program, resulting in a drastic reduction of corrosion? Note that periodically lubricating moving parts can reduce damage to coated surfaces.
Windows | Have corrosion-resistant materials been selected consistent with the ESC Zone or micro-environment? |  |  | UFC 3-101-01 Architecture; UFGS-08 56 53 BLAST RESISTANT TEMPERED GLASS WINDOWS; UFGS 08 51 13 Aluminum Windows; UFGS 08 51 23 Steel Windows; UFGS-08 53 00 PLASTIC WINDOWS; UFGS 08 52 70 Wood Windows - Repair And Rehabilitation; see also MDACS applicable sections
Have corrosion-resistant bolts or machine screws been selected and used?
| Have corrosion-resistant steel hinges been utilized for venting sash? |  |  | UFGS 08 52 00 Wood Windows
| Have corrosion-resistant fasteners and anchors been selected and utilized? |  |  | UFGS 08 52 00 Wood Windows
| Have corrosion-resistant steel slides been selected and utilized for horizontal sliding windows? |  |  | UFGS 08 52 00 Wood Windows
Hardware | Have the appropriate locks, latches, hinges, electrical hardware, knobs been selected consistent with the ESC Zone and micro-environment? |  |  | UFGS 08 71 00 Door Hardware
Roofing
| Has the following been considered in the design, construction and sustainment of the roofing system: • Careful system and material selection, design, contract document preparation, specification, installation, and maintenance • Considered weathering, corrosion, ultraviolet radiation, durability, and life cycle • Incorporated systems and details to meet environmental corrosivity conditions for the specific project location, as defined by Environmental Severity Classification (ESC) (See UFC 1-200-01 for ESC designations for DoD worldwide locations and the International Organization for Standardization [ISO] Corrosion Category Estimation Tool [ICCET]) • Humidity conditions considered during roof design; humid locations are those in ASHRAE climate zones 0A, 1A, 2A, 3A, 3C, 4C, and 5C, as identified in ASHRAE 90.1 • Considered protective metal coatings, types of steel and aluminum and influenced by ESC Zone • For roofs larger than 15,000 square feet or are classified as "critical use" or "mission critical", a registered roofing consultant (RRC), registered professional engineer (PE), or registered architect is required on the design team |  |  | See UFC 3-110-03 Roofing
| Has the design and subsequent construction included: • Installation of snow and frost barriers • Appropriately sized, located and installed guttering and downspouts • Parapet walls, if used, are well-designed to be able to be routinely cleared of debris • Minimized the use of interior down spouts • Conformed to good engineering practice for nail patterns and attachments • Used fasteners consistent with the material type to ensure that dissimilar metal corrosion is prevented • Ensured construction quality that is consistent with the contracted design • Ensuring the roofing design is appropriate for the environmental factors associated with that region (weather, wind, and precipitation) |  |  | See the CPC Source - Corrosion Issues in Roofing Systems Knowledge Area for more insights.
Does the maintenance and operations program for the installation include a roofing inspection and repair program? Does it also include: • Well-maintained gutter, downspout and valleys • Minimized foot traffic over roof areas that can possibly cause damage to membranes • Inspection of roofing undersides for possible leaks • Minimizing roof penetrations to support roof-mounted equipment (these must be inspected and fully resealed over time, not just at construction turnover) • Rooftop mechanical equipment discharge, particularly condensate water, is piped directly into roof drains avoiding continuous condensate leaks that can damage the roof membrane.
| Are drainage structures (drains, gutters, downspouts, drain pipes, parapet wall drains) maintained and kept clear from debris, silt, and other obstructions? |  |  | UFC 1-200-01 DoD Building Code, UFC 3-101-01 Architecture, UFC 3-110-03 Roofing
Have the effects of asphalt binder breakdown, loss of flexibility, cracking of roofing materials been factored into the design, construction and sustainment?
Have environmental risks including humidity, rain, condensation, biological growth, erosive forces, ultra-violet exposure and heat been factored into the design, construction and sustainment?
Has barrier failure endangering structural integrity and interior safety (e.g., mold and mildew) been factored into the design, construction and sustainment?
Protective Coatings and Paints
UFC 3-190-06 Protective Coatings and Paints; UFGS 09 90 00 Paints and Coatings; UFGS 09 96 00 High-Performance Coatings; UFGS 09 96 59 High-Build Glaze Coatings; UFGS 09 97 10.00 10 Metallizing: Hydraulic Structures; UFGS 09 97 02 Painting: Hydraulic Structures; UFGS 09 97 13.00 40 Steel Coatings; UFGS 09 97 13.15 Epoxy/Fluoropolyurethane Interior Coating of Steel Petroleum Fuel Tanks; UFGS 09 97 13.16 Interior Coating of Welded Steel Water Tanks; UFGS 09 97 13.17 Three Coat Epoxy Interior Coating of Welded Steel Petroleum Fuel Tanks; UFGS 09 97 13.25 Maintenance, Repair, and Coating of Tall Antenna Towers; UFGS 09 97 13.26 Coating of Steel Waterfront Structures; UFGS 09 97 13.27 Exterior Coating of Steel Structures; UFGS 09 97 13.28 Protection of Buried Steel Piping and Steel Bulkhead Tie Rods; UFGS 09 97 23.16 Linseed Oil Protection of Concrete Surfaces; UFGS 09 97 23 Metallic Type Conductive/Spark Resistant Concrete Floor Finish; AR 420-1 Facilities Engineering: Army Facilities Management.
| Is a program in place to monitor all protective coating operations? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control, para 4.5; UFC 3-570-06, App A1, para 2.e
| Are premature protective coating failures properly investigated, and is corrective action promptly taken? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control, para 3.4.4
Has the following evaluation to be made, per UFC 3-190-06? | "Provide paints and coatings that are durable and minimize the need for preventative and corrective maintenance over the expected service life of the component or system. Different materials will be used based on local environmental conditions. UFC 1-200-01, section titled 'Corrosion Prone Locations' identifies corrosive environments and humid locations requiring special attention. Corrosive environments, which require additional corrosion protection, are those project locations which have an Environmental Severity Classification (ESC) of C3, C4 or C5. To determine ESC for specific project locations, refer to UFC 1-200-01 Appendix titled 'Environmental Severity Classifications (ESC) for DoD Locations'. Humid locations are those in ASHRAE climate zones 0A, 1A, 2A, 3A, 3C, 4C, and 5C (as identified in ASHRAE 90.1)."
| Have the paints and coatings been fully evaluated as delineated in the previous row? Has that evaluation resulted in a paint or coating consistent with the requirement, surface characteristics, ESC Zone, and maintenance strategy for the protection from, and mitigation of, corrosion for facilities, facility components and infrastructure? |  |  | UFC 1-200-01 DoD Building Code; see Paints and Coatings Suite of Continuing Education Courses (WBDG.org)
Have the related criteria and standards been assessed and understood (Unified Facility Criteria (UFC), Unified Facility Guide Specifications (UFGS), Association for Materials Protection and Performance (AMPP)(Society for Protective Coatings (SSPC), National Association of Corrosion Engineers [NACE] International)) along with the tools for selecting paints and coatings?
| Has the proper surface preparation been achieved based upon the following factors to support the application of the paint/coating: Type of substrate, surface condition, type of exposure (service conditions), desired life of the coating or structure, coating to be applied, environmental constraints, aesthetic requirements, desired finish, and life-cycle cost considerations? |  |  | See also UFC 3-190-06 for additional details for coating removal and surface preparation.
Have the commonly used methods of surface preparation for coating listings in UFC 3-190-01 been reviewed and applied?
Have surfaces been repaired and properly prepared prior to application of new coatings?
| Have concrete surfaces been tested for moisture content? |  |  | ASTM D4263, ASTM F1869
Has any mildew been removed prior to painting?
In selecting paints and coatings, has the designer/ engineer considered and addressed: | 1. Environmental stewardship, durability and economics that requires choosing a paint system to minimize environmental impact while maximizing the life cycle. The economic analysis should cover initial and follow-on coatings across the entire life cycle, not just the initial coating. 2. Green building and certification systems, environmentally-friendly paint, and energy-efficient coatings. |  |  | AMPP Standards that apply to the Paints and Coatings Checklist include: SP 1 Solvent Cleaning; SP 2 Hand Tool Cleaning; SP 3 Power Tool Cleaning; SP 6/NACE 3 Commercial Abrasive Blasting; SP 7/NACE 4 Brush-off (Abrasive Blasting); SP 14/NACE 8 Industrial Abrasive Blasting; SP 15 Commercial Grade Power Tool Cleaning; SP 16 Brush-off Non-Ferrous Metals (Abrasive Blasting); SP 11 Power Tool Cleaning to Bare Metal; SP 10/NACE 2 Abrasive Blast to Near-White Metal; SP 5/NACE 1 Abrasive Blast to White Metal; SSPC/NACE Blast Standards; PA 1 Shop, Field, and Maintenance Painting of Steel; PA 2 Procedure for Determining Conformance to Dry Coatings Thickness; NACE SP0188 Discontinuity (Holiday) Testing of New Protective Coatings on Conductive Substrates
In high-traffic areas, such as interior doors and frames, has a solvent-based coating that may be the best choice for both performance and environment been considered?
| Have the requirements in the UFC been addressed to include the AMPP/SSPC Painting Contractor Certification Program, the AMPP/NACE QC Inspector Program and guidance on corrosion, cathodic protection, rust, deterioration, mold, mildew, and coatings? Note that the new UFC has not been issued. Revise this entry when it has been published (3/2/21) |  |  | UFC 3-190-06 Protective Coatings and Paints
| Have the contractor qualification requirements (AMPP/SSPC, AMPP/NACE, and AMPP/MPI Standards SSPC QP 1, QP 2, etc.) delineated in criteria been considered? |  |  | UFC 3-190-06 Protective Coatings and Paints, UFGS 09 90 00 Paints and Coatings, AMPP/SSPC-ACS 1/NACE No. 13 and appropriate corporate certification.
| Has the guidance on “special coatings […] required for harsh indoor locations or operations (any area subjected to chemical and/or abrasive action), and all outdoor installations” been addressed? Note that special coatings require compliance with AMPP/MPI Standards in the AMPP/MPI Approved Products List and the AMPP/MPI Architectural Painting Specification Manual prior to the start of any project. Is a skilled applicator requirement for coating application included? Have degradation, coatings, corrosion, rust, and ultraviolet topics been addressed? |  |  | UFGS 09 96 00 High-Performance Coatings
| Have “the requirements for epoxy-polyamide, polyurethane, and epoxy polyester high performance, architectural wall coating systems for interior and exterior surfaces” been considered and addressed? |  |  | UFGS 09 96 59 High-Build Glaze Coatings
| Have the “requirements for the preparation of surfaces and the application of paints for hydraulic structures and appurtenant items" been considered and addressed? Note that the UFGS addresses contractor qualifications and certifications (AMPP/SSPC QP 1, QP 2, QP 3). |  |  | UFGS 09 97 02 Painting: Hydraulic Structures
| Have “the requirements for preparation of surfaces and application of metallized coatings for hydraulic structures" been considered and addressed? Note that the UFGS addresses contractor qualifications and experience (AMPP/NACE Basic, Coating Inspector Training and Certification Program, etc.). |  |  | UFGS 09 97 10.00 10 Metallic Coatings for Hydraulic Structures
| The UFGS describes “the requirements for a Low VOC (< 50 grams/liter) two-coat polysulfide modified novolac epoxy [PMNE] coating [system] for interiors of newly constructed, Navy bulk fuel storage tanks”. Notes in the UFGS discuss maintenance coating design. Contractor qualifications and experience (SSPC QP 5, MPCAC-C14) are delineated. Have these requirements been considered and addressed? |  |  | UFGS 09 97 13.15 Low VOC Polysulfide Interior Coating of Welded Steel Petroleum Fuel Tanks
| The UFGS “covers the requirements for polyamide epoxy coating system[s] for interior of newly constructed Navy and Air Force water tanks, potable and non-potable, where shop applied coatings are not being considered”. It addresses contractor qualifications and experience (SSPC QP 5, SSPC C-7). Have these requirements been considered and addressed? |  |  | UFGS 09 97 13.16 Interior Coating of Welded Steel Water Tanks
| The UFGS describes requirements when using three-coat epoxy systems for interior coatings of newly constructed Air Force bulk fuel storage tanks. It addresses contractor qualifications and experience (SSPC QP 5, SSPC QP 1 and SSPC QS-1). Have these requirements been considered and addressed? |  |  | UFGS 09 97 13.17 Three Coat Epoxy Interior Coating of Welded Steel Petroleum Fuel Tanks
| The UFGS “covers the requirements for coating of new, and repairs to existing, steel towers”. It addresses contractor qualifications and experience (SSPC QP 2). Have these requirements been considered and addressed? |  |  | UFGS 09 97 13.25 Maintenance, Repair, and Coating of Tall Antenna Towers
| The UFGS describes “requirements for using coating new or existing steel-sheet piling and other steel waterfront structures. This coating system may also be used for repairing and coating of aged surfaces”. The UFGS lists qualifications and submissions requirements for contractors (SSPC QP 5, C 7, MPCAC). Have these requirements been considered and addressed? |  |  | UFGS 09 97 13.26 Coating of Steel Waterfront Structures, Zero VOC, (SZC) Splash Zone Coating
| The UFGS “covers the requirements for using zinc-rich epoxy/epoxy/polyurethane coating systems for exteriors of new Navy and Air Force steel structures, such as fuel tanks, water tanks, [and] aboveground piping”. Extensive notes at the beginning of the UFGS describe special requirements and recommendations. Contractor qualifications and certifications include SSPC PCS and SSPC QP 5. Have these requirements been considered and addressed? |  |  | UFGS 09 97 13.27 Exterior Coating of Steel Structures
| The UFGS “covers the requirements and application methods for tape wrapping systems that establish exterior protection of buried steel piping and steel bulkhead tie rods that rest above the reference level, 600 mm [2 feet] below Mean Low Water [MLW] or Mean Lower Low Water [MLLW], and for tape coating of buried steel pipe covered with an adhesive thermoplastic resin coating system, a thermosetting epoxy coating system, or a polyethylene-butyl adhesive system”. The UFGS states, “Inspection shall be performed by a [AMPP/NACE-]certified inspector”. Have these requirements been considered and addressed? |  |  | UFGS 09 97 13.28 Protection of Buried Steel Piping and Steel Bulkhead Tie Rods
| The UFGS provides guidance on “the requirements for coating systems, materials, surface preparation, and application of protective coatings on carbon steel”. Have these requirements been considered and addressed? |  |  | UFGS 09 97 13.00 40 Steel Coatings
Has the designer/ engineer: | Assessed and quantified coating CPC requirements by: 1. Identifying coating type and age? 2. Identifying coating defects and extent of work? 3. Identifying causative problems to include consulting with subject matter experts if needed? 4. Developing a remediation plan?
For Paints and Coatings QC, QA, Cx: | 1. Verify that the work is being performed according to contract requirements, plans and specifications 2. Ensure quality control through key inspection hold points 3. Ensure that premature coating failures do not occur 4, Document the inspections and types of materials used 5. Include a warranty inspection requirement
For Paints and Coatings QC, QA, Cx: | For surface preparation, address: 1. Treating surface irregularities such as holes, weld spatter, sharp edges, and corners 2. Cleaning and removing surface contaminants to the desired level 3. Producing a surface profile or texture for good adhesion of coatings |  |  | The guides include: AMPP/SSPC VIS 1 - Abrasive Blasting AMPP/SSPC VIS 3 – Hand and Power Tool Cleaning AMPP/SSPC VIS 4/NACE VIS 7 – Water Jetting AMPP/SSPC VIS 5/NACE VIS 9 – Wet Abrasive Blasting (WAB)
For Paints and Coatings QC, QA, Cx - Considerations for choosing a method for cleaning and removal of surface contaminants include: | 1. The type, amount, and adherence of the contaminant 2. The service environment 3. Any difficulties accessing areas for surface preparation and recoating applications 4. The type of coating system selected and its required service life |  |  | The guides include: AMPP/SSPC VIS 1 - Abrasive Blasting AMPP/SSPC VIS 3 – Hand and Power Tool Cleaning AMPP/SSPC VIS 4/NACE VIS 7 – Water Jetting AMPP/SSPC VIS 5/NACE VIS 9 – Wet Abrasive Blasting (WAB)
For Paints and Coatings QC, QA, Cx - Methods for cleaning and removal of surface contaminants include: | 1. Solvent cleaning 2. Chemical stripping 3. Hand tool cleaning and power-tool cleaning for removing loose rust, mill scale and paint 4. Low- and high-pressure water jetting 5. Abrasive blasting 6. Wet abrasive blasting, which is a mixture of abrasives and water |  |  | The guides include: AMPP/SSPC VIS 1 - Abrasive Blasting AMPP/SSPC VIS 3 – Hand and Power Tool Cleaning AMPP/SSPC VIS 4/NACE VIS 7 – Water Jetting AMPP/SSPC VIS 5/NACE VIS 9 – Wet Abrasive Blasting (WAB)
Applicators are often given choices of application methods and must decide the best method for a particular job. Factors that should be accounted for when choosing an application method include: | 1. Appropriateness for the coating type 2. Structural component size, configuration, and irregularities 3. Desired appearance 4. Access to the workpiece 5. Speed, ease, and economics of application method, including the coverage rates and transfer efficiency 6. Simplicity of equipment and applicator skills 7. Safety 8. Environmental requirements 9. Weather |  |  | AMPP/SSPC-PA 1; AMPP/SSPC-PA 2; ASTM D7091
To ensure that successful paints and coatings projects for facilities are realized, the following actions are recommended: | 1. Addressing coatings requirements early in the design process 2. Understanding the environmental stressors and severities
To ensure that successful paints and coatings projects for facilities are realized, the following actions are recommended: | 1. Ensuring that all requirements are covered in the project specifications, project order, or shop’s work order: a. Paint selection and appropriate application methodology explanations, including qualifications, testing, and inspection hold/check points b. Surface preparation requirements c. Application requirements d. Referenced industry standards
Ensuring that the sustainment program includes periodic inspection, evaluation, and maintenance of coated structures and coating systems requires that: | 1. Employing or contracting trained coating inspectors 2. Establishing a coating-degradation-evaluation process 3. Leveraging the knowledge gained through predictive maintenance to: a. Utilize sustainment management systems to document condition surveys b. Identify sustainment investment points balancing operational readiness, LCC, service life, and safety
For specific areas such as swimming pools, have chemically resistant finishes for concrete floors, fouling-resistant coatings, mildew resistant coatings, pavement markings, towers, tanks, storage distribution lines, etc., been assessed and the appropriate coating been selected and applied?
Mechanical Systems (See Note 5 at the beginning of this Checklist (3) "Micro-environments")
| Exterior and interior components exposed to outside ventilation are susceptible to corrosion. Has the design factored the impacts of airborne corrosive pollutants, condensation, leaks, temperature, moisture, poor humidity control, corrosive chemical reactions, abrasion, pitting, galvanic corrosion, mold, mildew, dissimilar metals, and corrosive soils affecting buried chilled water lines? Have the temperature differentials of air, liquid, and/or gas in ducts and conduits, as well as in the surrounding environment, been addressed in the design? |  |  | UFC 1-200-01 Building Code, UFC 3-190-06 Protective Coatings and Paints; UFC 3-410-01 Heating Ventilation and Air Conditioning Systems, UFC 3-410-04 Industrial Ventilation, UFC 3-430-01FA Heating and Cooling Distribution Systems, UFC 3-101-01 Architecture; UFC 3-420-01 Plumbing Systems; UFC 3-401-01 Mechanical Engineering; AR 420-1 Facilities Engineering: Army Facilities Management
Has the system been designed to manage condensation, humidity, airborne contaminants, chloride-containing environments, poor air quality, dissimilar metals, microbiologically induced corrosion, mold, and mildew? Have they been included in the SRM planning and execution?
Have the negative impacts to health, structural integrity, safety, sustainment costs, life cycle, and interrupted operations that require HVAC been factored into the design? Because humidity and temperature control for a well-managed and balanced HVAC system are so important to building integrity and health, have these issues been addressed in sustainment and life cycle planning and execution? Have the effects of HVAC on every aspect of the building envelope been considered and included in the design and SRM program?
Cooling Towers, Condensing Units
| Confirm tower has been constructed in accordance with specifications (e.g., galvanized, stainless steel, fiberglass). |  |  | See Corrosion section in UFC 3-410-01 Heating, Ventilating, and Air Conditioning Systems
Chemical treatment for HVAC Systems: If required, verify chilled and hot water systems have been provided with automatic chemical treatment system for the control of pH, scale formation, and corrosion inhibition
Finish: If indicated, verify anti-corrosion coating provided is immersion applied, baked phenolic, or other approved coating. Field-applied coatings are not acceptable.
Terminal & Package Units
| Where required, verify anti-corrosion coating provided on the casing and both the condenser and evaporator coils to protect against salt air damage. |  |  | UFC 3-410-01 Heating, Ventilating, And Air Conditioning Systems
Verify anti-corrosion coating is immersion applied, baked phenolic or other approved coating. Field applied coatings are not acceptable.
Interior spaces with high humidity, plumbing & fixtures (e.g. chemical storage, swimming pool enclosures, chemical treatment areas, research labs, etc.) (See Micro-environment description for Mechanical Systems); Exterior plumbing swimming pools recreational facilities
| Enclosed spaces that utilize and store corrosive chemicals must be designed with materials and components that are appropriately corrosion-resistant. Cheaper materials and components do not provide appropriate corrosion resistance. Because many chemicals, such as chlorine, are dangerous, storage and utilization must be consistent with criteria. robust. Surfaces that could be impacted include doors, valves, structural elements, and the mechanical equipment in the enclosed space. |  |  | UFC 3-420-01 Plumbing Systems; UFC 4-750-07 Recreational Aquatic Facilities; UFGS 22 00 00 Plumbing; UFC 4-740-02 Fitness Centers; AR 420-1
Control systems, when exposed to moisture, heat and corrosive chemicals, deteriorate quickly, affecting system operation. Have these risks been factored into the design, construction and sustainment?
Have the following environmental risks been factored into the design, construction and sustainment: Chloride-containing environments, humidity, temperature, leaks, poor air circulation, airborne corrosive pollutants, structural, applied chemicals and contaminants, inadequate or malfunctioning CP, internal corrosion (H2S, H2O, microbiologically-induced corrosion), poor design geometrics and construction practices, dissimilar metals causing galvanic corrosion, and water entrapment and intrusion?
Energy Supply Systems
Heat Pumps - Ground Source: | Finish - If required, verify anti-corrosion coating provided is immersion applied, baked phenolic, or other approved coating. Field-applied coatings are not acceptable.
Heat Pumps - Water Source: | Finish - If required, verify anti-corrosion coating provided is immersion applied, baked phenolic, or other approved coating. Field-applied coatings are not acceptable.
Heat Pumps - Air to Air: | Finish - If required, verify anti-corrosion coating provided is immersion applied, baked phenolic, or other approved coating. Field-applied coatings are not acceptable.
Mold & Mildew Review, Assessment (See Facility Assessment Checklist Sheet (this file)) (See also Fungi, Mold, & Mildew Corrosion Issues Knowledge Area)
| Have mold and mildew issues, including preventive measures, been researched and addressed? |  |  | UFC 3-101-01 Architecture; UFC 3-420-01 Plumbing Systems; UFC 3-401-01 Mechanical Engineering; UFC 3-410-01 Heating, Ventilating, and Air Conditioning Systems; Industrial Ventilation; AR 420-1 Facilities Engineering: Army Facilities Management
Have the UFC 1-200-01 DoD Building Code requirements for design in a corrosion prone location been followed and incorporated? This includes ESC Zone requirements and ASHRAE Humid location climate zones and interior area guidance. Other areas that are identified include: 1. Design Geometries 2. Humidity Resistance 3. Elevated Temperatures 4. Buried or submerged structures and systems
Have the requirements in UFC 3-190-06 Protective Coatings and Paints been followed and incorporated?
Has sufficient ventilation been provided to prevent the occurrence of mold and mildew?
| The Fungi, Mold and Mildew Corrosion Issues Knowledge Area provides extensive insights into this topic as well as providing a handbook of sorts in the identification, testing and cleanup/remediation of mold and mildew in facilities. |  |  | See: https://www.wbdg.org/ffc/dod/cpc-source/fungi-mold-mildew-knowledge-area
Have the 4 Ds of Moisture Management been followed and addressed: • Deflection of water to minimize wetting exposure • Drainage to convey away water that penetrates the assembly • Drying of any residual water by means of ventilation • Durability of materials to withstand exposure to periodic wetting and provide an acceptable service life
Have air leakage issues in the building envelope which contributes to moisture problems within the building enclosure been analyzed and addressed? Those problems include: 1. Mold and durability in exterior walls and wall cavities connected to the exterior 2. Excessive rain penetration into wall cavities 3. Poor indoor temperature and humidity control 4. High heating and air conditioning costs 5. Compromised noise, fire and smoke control measures 6. Spalling of masonry, premature corrosion of metal parts in exterior walls, high wood moisture content and rot and in colder climates icicles on exterior facades 7. Air in hot humid climates can cause mold due to condensation on cooler surfaces
Have the following mold and mildew effects on mission and operations been considered and resolved: • Negative effects to health, morale, safety, maintenance costs, disruption of services to supported systems, sustainment costs, life cycle, & interrupted operations that require well-functioning HVAC and moisture/humidity control. • Once mold and mildew have been identified, facility quarantine may be necessary to remove and clean contaminated surfaces and materials. • The area may require industrial hygiene air quality and surface readiness clearances. • Building enclosure integrity affects every aspect of the building envelope. • Water, waste, ducting conduits all must be appropriately designed and functioning allowing for the prevention of moisture and air infiltration, removal of condensate and overflow to avoid mold and mildew growth conditions.
Have the following actions been pursued to help reduce the intrusion of moisture intrusion (leaks, humidity, condensation) into the building envelope: • Correctly designed, constructed, and maintained roofs and the associated components • Ensuring that construction quality is consistent with the contracted design, paying special attention to HVAC air balancing, caulking/sealing, condensate/moisture removal, inspection of drip pans and drains, moisture barriers • Inspecting and correcting roofing undersides for possible leaks • Ensuring that the building envelop components are appropriate for the ESC factors required for that region (weather, temperature, wind, precipitation and the associated materials and designs) • Minimizing roof and wall penetrations to support roof mounted equipment (note these must be inspected and fully resealed over time (throughout the life cycle)) • Installing and maintaining windows, doors and other wall penetrations • Paying close attention to window and door flashings and the associated water drainage
Have the following actions been pursued to help reduce the intrusion of moisture intrusion (leaks, humidity, condensation) into the building envelope: • Ensuring that there is a continuous air barrier to prevent air leakage into or out of conditioned spaces to include checking for and repairing seals • Ensuring that transitions from one building element to the next, such as wall to roof and wall to openings, are carefully designed and constructed • Ensuring that the portion of the structure in contact with the ground (slab on grade, basement, structural elements) is constructed and maintained to minimize water intrusion. This includes providing foundation drainage and moisture management systems, installing sump pumps with backup power where needed, sheet drainage material installed over exterior insulation, footing drains, waterproofing, air sealed rim/band joist and sill plate. Each location should be assessed for the required combination of foundation and basement moisture management requirements. • Ensuring that rainwater is directed well away from the foundation and that site drainage takes water away from the structures • Providing a continuous air barrier • Operation and balancing the HVAC system to include humidity control, duct sealing, and moisture removal • Address specific building and room uses and provide appropriate levels of HVAC moisture control and mold resistant materials consistent with the risk and local environment
For maintenance management programs include: • Fix leaky plumbing and leaks in the building envelope as soon as possible. • Watch for condensation and wet spots. Fix source(s) of moisture problem(s) as soon as possible. • Prevent moisture due to condensation by increasing surface temperature or reducing the moisture level in air (humidity). To increase surface temperature, insulate or increase air circulation. To reduce the moisture level in air, repair leaks, increase ventilation (if outside air is cold and dry), or dehumidify (if outdoor air is warm and humid). • Keep heating, ventilation and air conditioning (HVAC) drip pans clean, flowing properly and unobstructed. • Vent moisture-generating appliances, such as dryers, to the outside where possible. • Maintain low indoor humidity, below 60% relative humidity (RH), ideally 30-50%, if possible. • Perform regular building/HVAC inspections and maintenance as scheduled. • Clean and dry wet or damp spots within 48 hours. • Don't let foundations stay wet. Provide drainage and slope the ground away from the foundation. • Repair rainwater leaks through walls. At windows and at roofs as they are frequently the most significant contributors of moisture. Also, houseplants and any source of standing water (such as aquariums and sumps) can contribute significant moisture to the air.
Causative factors for moisture problems may include and must be considered: • Roof leaks • Landscaping or gutters/downspouts that direct water into, against the foundation, or under the building • Delayed maintenance or insufficient maintenance are also associated with moisture problems in schools and large buildings • Condensation associated with high humidity or cold spots in the building (ex. unvented combustion appliances) • Localized flooding due to: o Plumbing failures or heavy rains o Slow leaks in plumbing fixtures o Malfunction or poor design of humidification systems
Have moisture and leak prevention measures been implemented to prevent mold and mildew?
Electrical Systems
| Electrical distribution systems have many components that are susceptible to corrosion and thus must be protected and maintained to ensure safe and reliable operation. These at-risk components include: Timber, concrete, and steel poles for above ground distribution lines and lighting, steel transmission towers and tower footings, guy anchors, grounding systems, substations, transformers (aboveground and submersible), cable, wire, and conductors, conduits and duct banks, manholes, and electrical panels. |  |  | UFC 3-430-09 Exterior Mechanical Utility Distribution, UFC 3-501-01 Electrical Engineering, UFC 3-550-01 Exterior Electrical Power Distribution, UFC 3-555-01N 400 Hertz Medium Voltage Conversion/Distribution and Low Voltage Utilization Systems, UFC 3-575-01 Lightning and Static Electricity Protection Systems, UFC 3-580-01 Telecommunications Building Cabling Systems Planning and Design, UFGS 09 96 00 High Performance Coatings, UFGS 09 97 13.00 40 Steel Coatings, UFGS 09 97 13.25 Maintenance, Repair, and Coating Of Tall Antenna Towers, UFGS 09 97 13.27 Exterior Coating Of Steel Structures, UFGS 26 11 14.00 10 Main Electric Supply Station and Substation, UFGS 26 56 00 Exterior Lighting, UFGS 33 05 16 Concrete Poles, UFGS 33 71 01.00 40 Overhead Transmission and Distribution
Electrical distribution systems are extensive and complex and must be managed well by facility professionals. Corrosion often occurs before it is noticed and can take many forms from pitting to uniform to galvanic across a broad range of exposures and environmental conditions. Vigilance and an effective SRM program, along with good design and construction, are essential for continuous responsiveness of electrical distribution systems.
Has the design addressed the impacts of chloride-containing environments, humidity, rain, salinity, structural loading, ultraviolet light exposure, applied chemicals and contaminants, erosive forces, soil corrosivity, inadequate or malfunctioning CP, internal corrosion (H2S, H2O, microbiologically induced corrosion), condensation, poor design geometrics and construction practices, dissimilar metal corrosion, water entrapment and intrusion?
Has the planning, design, construction and sustainment program ensured that the electrical distribution systems are addressed holistically in the context of providing essential power to all facilities? Airfield lighting, shore power at dockside, security systems, control systems for waste removal, water supply, natural gas supply, etc. are affected by electrical power. System failures in whole or in part can be hugely disruptive to the mission and create health and safety concerns. Utility system reliability is critically important.
Have the major corrosion factors for electrical distribution systems been considered and addressed: | Atmospheric corrosion on aboveground structures; soil corrosive properties and stray currents for buried or submerged structures; insect and fungi attack on timber distribution poles; dissimilar metals in contact; non-compatible materials; and high current densities at bonding and grounding locations. Note: To resist decay from insects and fungi, timber poles must be pressure treated full length with chromated copper arsenate or ammoniacal copper arsenate according to AWPA U1. Cuts and bores in timber poles should be done prior to treatment.
| Have the corrosion inspections required by P-604 been conducted? Note that these inspections are focused on shore power cable assemblies, receptacles, and connections. |  |  | P-604 Electrical - Safe Acts for Employees (E-SAFE), NFPA 70E Standard for Electrical Safety in the Workplace
Cathodic Protection
| Common systems and structures requiring protective coatings and CP regardless of soil or water corrosivity include: Natural gas piping and distribution systems; liquid fuel piping; oxygen piping; fire mains and underground fire protection piping; systems with hazardous products; ductile iron pressurized piping under floor (slab on grade); underground heat distribution and chill water piping in metallic conduit; and underground, ground level, and elevated storage tank systems. Other systems that may employ CP include potable-water distribution systems, sewage lift stations, and compressed-air distribution systems. |  |  | (UFC 3-570-01) Cathodic Protection; UFC 3-570-06 Operation and Maintenance: Cathodic Protection Systems; (UFC 3-570-06) by Galvanic Anodes & Impressed Current; UFGS 26 42 (13 though 22) Cathodic Protection Specifications. Note, as identified below the Services might have additional clarifying guidance, AR 420-1 Facilities Engineering: Army AF 32-1054 Facilities Management; Civil Engineer: Corrosion Control
| Have the CP systems been carefully designed, correctly installed, inspected for proper function, certified to deliver adequate protection and maintained. Current AMPP/NACE standards recognize adequate protection through three primary criteria for steel exposed to soil environments: 1. -850 mV structure-to-electrolyte (S/E) potential or more negative, with respect to a copper/copper-sulfate electrode (CSE), with current applied; 2. -850 mV CSE polarized S/E potential or more negative; and 3. +100 mV polarization shift or greater. Meeting any one of the above criteria indicates adequate CP. |  |  | AMPP/NACE International SP 0169 (2013). “Control of External Corrosion on Underground of Submerged Metallic Piping Systems.” NACE International.
Have the following methods of Corrosion Control in the Waterfront and Coastal Zone been considered: • Altering the Environment • Good Design Practices with design geometrics considerations • Corrosion Allowance • Material Selection • Protective Coatings • Cathodic Protection
Have the following examples of Altering the Environment been considered: • Using a selective backfill around a buried structure • Using corrosion inhibitors such as fuel additives • Modifying the structure to provide adequate drainage • Relocating sources of stray currents • Reducing wave action and erosion with the addition of breakwaters, groins, jetties, rip rap, and stone revetments
A cathodic protection system can be rendered fully or partially inoperative due to a lack of maintenance and repair which is all too common. Have the following actions been included in CP planning, design, and management: - Regularly scheduled maintenance inspections are recommended to minimize risk of failure of the cathodic protection system. -Coatings and CP should most always be used in conjunction with each other for buried or submerged structures. Both are required by law for Underground Storage Tanks (UST) and certain Petroleum, Oil and Lubricant (POL) lines.
When designing or evaluating a CP system, have the CP design objectives: | Provided sufficient, continuous current density to all parts of structure to acceptable criteria?
Minimized interference effects to other structures?
Provided operational flexibility for expected changes in environmental, protective coating, and system service life?
Adhered to applicable codes and standards to ensure public and operational personnel safety?
Provided CP system design life that coincides with the protected system's service life?
Provided testing and monitoring facilities to ensure CP system performance meet industry criteria, standards, and regulations?
Cathodic protection is utilized to protect critical infrastructure, much of which would have calamitous results if their structures were to fail. | Have the following systems been considered, reviewed and issues addressed?
Natural gas piping and distribution systems
Liquid fuel piping
Oxygen piping
Fire mains and underground fire protection piping
Ductile iron pressurized piping under floor slab (slab on grade)
Underground heat distribution and chill water piping in metallic conduit
Steel sheet pile seawalls, pier support, fender piles, and other submerged steel structures
Underground, ground level and elevated storage tank systems
Other systems that may employ CP: | Have the following systems been considered, reviewed and issues addressed?
Systems with hazardous products
Potable water distribution systems
Compressed air distribution systems
Sewage lift stations
Concrete reinforcing steel
Measurement Planning | The main method is the measurement of the structure-to-electrolyte (S/E) potential as compared to the selected criteria.
The system currents can also be measured as an additional performance parameter.
Another approach is to routinely measure S/E potentials for compliance with these criteria and ensure meeting any regulatory standards.
Any of those factors that affect polarization, potential measurements, and criteria validity must be taken into account.
Does the CP system design: | Provide sufficient, continuous current density to all parts of structure to acceptable criteria?
Minimize interference effects to other structures?
Provide operational flexibility for expected changes in environmental, protective coating, and system service life?
Adhere to applicable codes and standards to ensure public and operational personnel safety?
Provide CP system design life that coincides with the protected system's service life?
Provide testing and monitoring facilities to ensure CP system performance meet industry criteria, standards, and regulations?
Is there a periodic inspection program to determine: | A properly designed, operated, and maintained CP system to include the replacement of CP components?
An annual maintenance and periodic repair program that reduces costs and plans for major repairs to or replacement of the structures themselves?
For CP and Protective Coatings: | Are CP and protective coatings provided on all metallic fuel storage tanks in contact with soil to include underground storage tanks (USTs), aboveground storage tanks (ASTs) and associated piping? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
| Are CP and protective coatings provided on interior water storage tanks and bottoms in contact with the soil? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
| Are CP and protective coatings provided on other buried utilities if the soil resistivity is below 10K ohm-centimeters? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
Ground rods and systems are designed for the soil condition and corrosivity of the Installation. Measures, such as installation methods, have been implemented to mitigate corrosion (such as use of copper ground rods, auguring, and backfill in desert locations). (Note: It has been discovered that there have been trouble with ground rods corroding in the desert. Auguring and use of copper to mitigate. The DWG is working issue in conjunction with Fence UFGS project currently underway.
Cathodic Protection Testing
| Do installed CP systems provide protective potentials per AMPP/NACE criteria, SP0169? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; AMPP/NACE International SP 0169 (2013). “Control of External Corrosion on Underground of Submerged Metallic Piping Systems.” AMPP/NACE International.
| Are CP systems inspected, tested and records kept as required per UFC 3-570-06? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems
| Are galvanic (sacrificial anode) systems being checked annually? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06, App A3
| Are impressed current systems being checked monthly and within 60 days of last Close Interval Survey (CIS)? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-06 O&M: Cathodic Protection Systems, App A2
| Are CISs being conducted every 5 years on all pipelines with CP? Also, are they conducted 30 days after a CP system installation? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; UFC 3-570-6 O&M: Cathodic Protection Systems
| Are annual water-tank calibrations being conducted? Also, are they conducted 30 days after a CP system installation? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
| Are annual impressed-current anode-bed surveys being conducted? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
| Are dielectric flanges and unions being tested annually? |  |  | Not required per AFI, but are helpful in CP work.
| Are other inspections and surveys documented using local forms and placed in the appropriate CP system folder? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
| Are waivers, deviations and/or omissions form standard design practices documented in the appropriate AST/UST records? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
Cathodic Protection Field Tests Prior to CP System Installation
Perform non-destructive testing of anodes
Perform destructive testing of anodes
Perform base potential tests, insulation joint testing, electrical continuity testing, pipe casing testing, anode-topsoil, potential tests, anode output tests, protected potential measurement tests, and interference testing
Perform field operation tests
Exterior Piping Cathodic Protection
If underground steel piping is installed, verify a cathodic protection system is provided.
If a cathodic protection system is provided, verify the system was designed by a AMPP/National Association of Corrosion Engineers (NACE) certified Cathodic Protection Specialist and this specialist supervised, inspected and tested the installation and performance of the CP System. Note that there are four AMPP/NACE CP certifications, but only the AMPP/NACE CP Specialist (CP4) certification demonstrates thorough knowledge of CP system design.
Verify test stations were mounted on posts and placed at the manhole or nearby building. Verify test stations were provided at each end of each cathodically protected section.
Fire Protection (FP) & Life Safety
Has the design addressed issues related to: | Component malfunction due to corrosion (e.g. sprinkler heads, valves, control systems, etc.) that impacts system operation and availability, risks to structure and life safety (See UFC 3-600-01), and moisture, salt water, salty air, inadequate coatings, and dissimilar metals? |  |  | UFC 3-600-01 Fire Protection Engineering for Facilities
Have considerations for moisture, salt water, salty air, inadequate coatings, and dissimilar metals been incorporated into the design and sustainment execution plan?
Asphalt Concrete & Portland Cement Concrete Pavements
| Have the referenced UFC(s) and UFGS(s) been reviewed and incorporated into the design, construction SRM or maintenance program? |  |  | UFC 3-250-01 Pavement Design for Roads and Parking Areas; UFC 3-250-03 Standard Practice for Flexible Pavements; UFC 3-250-04 Standard Practice for Concrete Pavements; UFC 3-270-01 O&M Manual: Asphalt and Concrete Pavement Maintenance and Repair; UFGS 03 30 00 Cast-in-Place Concrete; UFGS 32 01 13.63 Gilsonite Modified Asphalt Emulsion Seal Coats; UFGS 32 13 13.06 Portland Cement Concrete Pavement For Roads and Site Facilities; Environmental Severity Classification variations (see Tables, UFC 1-200-01 DoD Building Code)
| Have the pavements been inspected and assessed for: 1. Asphalt binder breakdown, loss of flexibility, cracking and pothole failure, base course and structural failure? 2. Concrete mix permeability and contaminants? 3. Corrosion in concrete-pavement reinforcing steel causing spalling and surface failure? 4. Alkali-silica reaction? |  |  | See Facilities Corrosion Impacts on Operations and Mission Table (https://www.wbdg.org/FFC/DOD/CPC/Facilities_Corrosion_Impacts_on_Operations_and_Mission_v3.pdf) on the CPC Source
Are the limitations and restrictions for Glass Fiber Reinforced Polymer. Reinforcement (GFRP) been reviewed, understood and followed?
Have corrosive factors such as degradation from ultraviolet radiation, corrosion of reinforcing steel (concrete pavements), chemical impacts (salt and other chemicals), heat impacts of jet blast, and freeze/thaw cycles been considered in the design?
For operational pavements such as airfields and critical road infrastructure, have the corrosion impacts causing possible loss of mission capability been assessed and incorporated in the design solution? For roads and related pavements, has the inability to support designed functions caused by corrosion related deterioration creating possible delays, congestion, disruption, access denial, and reduced safety been incorporated into the design?
Has the Portland Cement Concrete Pavement structure been inspected, and have the following issues been identified: | Cracking, spalling, pumping, buckling, material related deterioration (alkali-silica reactivity, durability cracking), surface distress, and shoulder erosion?
For Portland Cement Concrete (PCC), have the following issues been considered and addressed: | 1. Integrity of the mix design? 2. Existence of supplementary cementitious materials (SCM) such as fly ash and other pozzolans? These materials are added to replace 15%-25% of the cement and help to reduce the PCC permeability and, as a result, reduce the corrosion potential of the reinforcement. 3. Slump within design tolerances? 4. Refraining from adding water on site to improve workability? (A lower water-cement ratio usually results in stronger and less permeable PCC.) 5. Proper placement of reinforcement bars and tendons with the appropriate minimum PCC cover? 6. Consolidation of PCC by eliminating voids through proper vibration and placement techniques? 7. Controlling and minimizing PCC cracking and surface imperfections? 8. Proper joint design and construction?
Has the Asphalt Concrete Pavement been assessed for distresses to include: | Fatigue (alligator cracking), block cracking, edge cracks, longitudinal (linear) and transverse cracking, reflection cracking, slippage cracks, corrugations (slippage) and shoving, rutting, settlements and grade depressions, upheaval, swell, utility cuts, patch failure, potholes, raveling, weathering, bleeding or flushing, polished aggregate, loss of aggregate on surface treatments, and longitudinal and transverse streaking?
Have the impacts of corrosion on readiness and associated risks been addressed for airfield runways, ramps, and critical road infrastructure to determine loss of mission capability affecting national defense: | 1. Foreign Object Damage (FOD) (spalling concrete, reinforcing steel expansion due to corrosion)? 2. Aircraft mooring and tie-down failure? 3. Corrosion-compromised embedment that can jeopardize the hold-down capacity of aircraft tie-downs? 4. Inability of roads and related pavements to support design functions (catastrophic corrosion induced structural failure)? 5. Bridge integrity that could provide access denial and risk of injury or death (see item 4)? 6. Structural integrity of waterfront-area pavements impacted by corrosion failures affecting the loss of mission capability, resupply capability, ship support and sustainment operations, and personal safety?
For Asphalt Concrete and Portland Cement pavements: | 1. Is there a Maintenance Operating Procedure (MOP)? 2. Is there a CPC plan for these pavements by function? 3. What is the reporting and data collection system utilized for pavements? 4. How easy is it to determine CPC deficiencies and maintenance planning, programming and execution associated with these pavements? 5. How effective is the Maintenance Operating Procedures (MOP) and associated execution?
Have these pavement-related corrosion stressors been addressed in the design, construction and SRM? | Thermal and photo oxidation, ultraviolet radiation degradation, ultraviolet radiation degradation, freeze-thaw (frost heave), corrosion of reinforcing steel, chemical impacts (salt and other chemicals), heat impacts of jet blast (surface breakdown, spalling, exposure of reinforcing steel and associated foreign object damage [FOD] risk), and interaction of aircraft and vehicles with the pavement (including friction loss, surface breakdown, and over-weight vehicle traffic).
Have these corrosion impacts on pavements been addressed in the design, construction and SRM? | AC binder breakdown, pavement hardening, embrittlement, loss of flexibility, cracking and pothole failure, base course and structural failure, spalling due to corrosion of steel in reinforced PCC, PCC mix permeability and contaminants, AC and PCC pavement surface failure, and alkali-silica reaction.
Bridges
| Have the following impacts been addressed in the planning, design, construction and SRM program? - Corrosion of metals to include PCC reinforcing, structural steel, bridge deck corrosion and erosion, and metallic connectors. Note that the condition of the wearing surface on a bridge is affected by the steel and other materials that are influenced by humidity, rain, chloride-containing treatments and environment, structural loading, applied chemicals, and erosive forces. - Paint failure, cathodic conditions. Leaking bridge joints allowing water, salts, & debris to fall to bridge components below. General uniform thickness loss or concentrated pitting. Stress corrosion cracks leading to fatigue growth & fracture. - Macro and micro bridge environment impacts and considerations - Loss of strength due to bridge system component failure - For timber bridges, bacteria, fungi, insects, mollusks, weathering, wetting, drying, chemical exposure and atmospheric contaminants. |  |  | AR 420-1 Facilities Engineering: Army Facilities Management
Has the designer/maintainer inspected and addressed the corrosion of metals to include concrete reinforcing, structural steel, bridge-deck corrosion, bridge-deck erosion, and metallic connectors?
Have humidity, rain, chloride-containing environments, salinity from deicing salts, structural loading, applied chemicals, and erosive forces been considered in the design/sustainment planning?
For project planning, design and sustainment have CPC factors including access denial, structural failure, inability to support designed functions creating delays, congestion, disruption, and reduced safety been considered and addressed? Note that catastrophic failures due to corroded metals, spalled concrete, reduced load carrying capacities, if left unchecked, will inhibit or deny the design load carrying capacity of the bridge.
Waterfront & Coastal Structures
| Waterfront structures are exposed to extreme corrosion, high structural deterioration causing failure, and sea-level rise (fixed elevation exposure to high salinity impacts from gradual and dramatic variations in sea level). |  |  | UFGS 03 31 29 Marine Concrete With Service Life Modeling; UFGS 03 31 30 Marine Concrete
Have humidity, rain, chloride-containing environments, salinity from deicing salts (especially salt water, dramatic shifts in tides), structural loading, applied chemicals, erosive factors, temperature, moisture, and water-borne pollutants been quantified and addressed? Waterfront utilities are particularly susceptible to atmospheric and salinity risks.
Have facility availability, high sustainment costs, reduced life cycle, structural degradation, shoreline erosion, reduced capacity and berthing availability been factored into the design, construction and sustainment?
Has the design, construction, QC, QA, Cx and SRM plans addressed the following: | Concrete testing: petrographic, chemical, service-life modeling?
Validating in-water/underwater structure complies with RFP requirements, including number, location, and size?
Inspecting in-water prestressed/precast concrete piles or sheet piles for alignment, spalls, cracks, damages, defects, lifting hoops cut/area patched, exposed steel ties, and penetrations?
Inspecting in-water cast-in-place concrete drilled caissons for alignment, spalls, cracks, damages, defects, concrete quality (hardness) and honeycombing?
Inspecting in-water steel piles and/or prestressed/precast concrete sheet piles for alignment, damage, buckling, coating damage, penetrations, and gaps?
Inspecting underwater concrete placement for defects such as honeycombing and concrete quality (hardness)?
Inspecting underwater cathodic-protection anodes and connections?
Have the following methods of CPC in the Waterfront and Coastal Zone been included in planning, design, construction and sustainment? | 1. Planning and applying CPC design and construction; 2. Selecting appropriate materials; 3. Using protective coatings; 4. Leveraging cathodic protection (for more information, review the Cathodic Protection Basics training module and the CP Knowledge Area); 5. Creating and managing an active Waterfront Sustainment, Restoration and Modernization (SRM) Program 6. Altering the Environment 7. Good Design Practices with design geometrics considerations 8. Corrosion Allowance 9. Material Selection |  |  | UFC 4-150-07 Maintenance of Waterfront Facilities UFC 4-151-10 General Criteria for Waterfront Construction UFC 4-150-02 Dockside Utilities for Ship Service UFC 4-152-01 DESIGN: Piers and Wharves UFC 3-570-01 Cathodic Protection UFC 3-570-06 Operation and Maintenance: Cathodic Protection Systems UFC 3-190-06 Protective Coatings And Paints UFGS 26 42 (13 though 22) Cathodic Protection Specifications UFGS 09 97 13.26 Coating of Steel Waterfront Structures, Zero Voc, Splash Zone Coating UFGS 35 59 13.14 20 Polymeric Fender Piles UFGS 03 31 29 Marine Concrete
Have the severity and stresses associated with the waterfront environment and the associated waterfront zones for the design, construction and sustainment of new and existing facilities been assessed and applied?
Have the right materials been selected, installed and maintained?
Have the high stress levels in the waterfront area for utility systems, pipelines, steel structures, concrete, reinforcing steel, and timber been thoroughly assessed and addressed? Note that typically, a higher degree of CPC is required for waterfront areas. For instance, concrete structures will require more cover over reinforcing steel and the addition of complementary cementing materials, such as fly ash to reduce permeability.
Have the enormous combination of materials to create a viable and productive fabric of facilities in the waterfront and coastal zone requires skill, coordination and current knowledge been assessed?
Is a Sustainment Management System (SMS) Program in place that includes inspections, planning and programming, maintenance and repair and associated data collection and management?
Are the information and guidance in UFC 4-150-07 Maintenance of Waterfront Facilities being followed?
| Corrosion-resistant material selection impacts distribution lines, supports, covers, and access panels, along with how each line connection is made, which also includes the appropriate grounding techniques. Attention to these details will ensure that the required utility services will be available on demand throughout the anticipated life cycle. Have these criteria been utilized in the waterfront project? |  |  | Corrosion prevention and control requirements for utilities in the waterfront area is required and is covered in UFC 4-150-02 Dockside Utilities for Ships Service, UFC 3-570-01 Cathodic Protection, and UFC 3-570-06 O&M: Cathodic Protection.
Aviation: Hangar & Flightline Facilities
| When viewed as a system, all facilities must function together to ensure a safe and ready operational environment. Other facilities, such as pavements, POL, storage, airfield lighting, and arresting gear, react to corrosive environments, especially where deicing and salt-laden air exposure occurs. |  |  | UFC 3-260-02 Pavement Design for Airfields; UFC 3-260-01 Airfield and Heliport Planning and Design; UFC 3-260-16 O&M Manual: Standard Practice For Airfield Pavement Condition Surveys; UFGS 32 13 13.43 High Temperature Concrete Paving For Airfields Using Lightweight and Traprock Aggregates; UFGS 32 13 14.13 Concrete Paving for Airfields and Other Heavy Duty Pavements
Have the following factors been considered during planning, design, construction and sustainment actions: humidity, rain, chloride containing environments, salinity from deicing salts, ultraviolet light exposure, condensation, structural, applied chemicals, microbiologically-induced corrosion, internal environments (especially for pipelines, utilities, ASTs and USTs), erosive forces, soil corrosivity, and heat and freeze/thaw impacts on pavements?
Corrosion-related operational impacts include any risk where one or more facilities that are in the process of keeping or sustaining an aircraft cannot meet required readiness levels. For example, runway integrity will be impaired by asphalt binder breakdown or concrete doweling corrosion that causes spalling and foreign object damage. Maintenance facility roof failure may affect health and safety (mold, mildew, HVAC air quality) or shop testing efficiency. Have these relationships been assessed and addressed during the life-cycle planning evaluation, design activities and sustainment activities?
For Aviation facilities: | 1. Is there a Maintenance Operating Procedure (MOP) for critical Systems?
2. Is there a CPC plan for these systems?
3. What is the reporting and data collection system?
4. How easy is it to determine CPC deficiencies and maintenance planning, programming and execution?
5. How effective is the MOP and associated execution?
| Hangar bays are considered exposed, exterior locations. Hangar bays have been designed, and components and systems within, are designed for the ESC location of the Installation. |  |  | UFC 1-200-01 Building Code
Exterior Structures & Facilities
Drainage Structures | 1. Have drainage issues been considered and addressed? 2. Does water drain away from structures and into drainage structures? |  |  | UFC 3‐201‐01 Civil Engineering
3. Are drainage structures (catch basins, gutters, curbing, drain pipes) maintained and kept clear from debris, silt, and other obstructions?
4. Is landscaping positioned to facilitate drainage away from the structure?
5. Are building materials selected to encourage drainage?
6. Are road structures (curbs, sidewalks, ramps, gutters, storm drainage) coordinated to ensure removal of rainfall?
Utilities and Buried Structures
| Note that this section overlaps with others in this checklist such as Cathodic Protection. The user will need to recognize the overlaps and leverage those by placing them in context with the system being assessed. Aboveground utilities are extensive and complex and create a major challenge for facilities professionals. Corrosion often occurs before it is noticed and can take many forms from pitting to uniform to galvanic across a broad range of exposures and environmental conditions. Vigilance and an effective SRM program, along with good design and construction, are essential for continuous system responsiveness. |  |  | UFC 3-190-06 Protective Coatings and Paints UFC 3-570-01 Cathodic Protection Design UFC 4-152-01 Design: Piers and Wharves UFGS 03 01 00 Rehabilitation of Concrete UFGS 09 90 00 Paints and Coatings UFGS 09 97 23.17 Corrosion Inhibitor Coating of Concrete Structures UFGS 09 97 13.26 Coating of Steel Waterfront Structures UFGS 09 97 13.27 Exterior Coating of Steel Structures UFGS 23 64 26 Chilled, Chilled-Hot and Condenser Water Piping Systems UFGS 26 42 15.00 10 Cathodic Protection System-Steel Water Tanks UFGS 33 61 13 Pre-Engineered Underground Heat Distribution System UFGS 33 61 13.19 Valves, Piping and Equipment in Valve Manholes AR 420-1 Facilities Engineering: Army Facilities Management
Underground Utilities & Buried Structures | Facilities that are out of sight create a challenge for facility managers. Are systems in place to inspect and assess the facility (e.g. CP, SCADA, etc.), including access points? Does the design minimize leaks and system failures caused by corrosive soils, chemicals, de-icing, poor construction, dissimilar-metal use and design geometrics? These factors can create a high probability of service interruptions.
Have soil corrosivity, structural forces, erosive forces, inadequate or malfunctioning CP, internal corrosion (H2S, H2O, microbiologically-induced corrosion), condensation, poor design geometrics, poor construction practices, dissimilar-metal corrosion, water entrapment and water intrusion been considered when designing or creating SRM actions?
Have the corrosion impacts on operational and health and safety been considered when planning, designing and sustaining buried facilities essential for supplying power, waste removal, water supply, and natural gas supply? Note that corrosive impacts causing system failures in whole or in part can be hugely disruptive to the mission and create environmental and health and safety concerns. Utility system reliability is critically important to mission effectiveness.
Where the utility is underwater: | Validate in-water/underwater components comply with RFP requirements, e.g., number, location, and size.
Inspect underwater component for defects/damages, cracks, missing anchors, and coating damage.
Have these factors been considered and addressed during the life cycle processes? | Utility systems are impacted by chloride containing environments, humidity, rain, salinity, structural loading, applied chemicals and contaminants, erosive forces, internal corrosion (H2S, H2O, microbiologically-induced corrosion), condensation, poor design geometrics, poor construction practices, dissimilar-metal corrosion, water entrapment and water intrusion.
Have these factors been addressed during operational project planning and design? | Aboveground facilities are essential for supplying power, waste removal, water supply, natural gas supply, etc. System failures in whole or in part can be hugely disruptive to the mission & create environmental and health & safety concerns. Utility system reliability is critically important and ESC Zone design requirements must be included in the constructed facility. CPC sustainment actions will continue to keep these facilities operational. Have these been considered and addressed?
Have the corrosive forces been identified, and have CPC design strategies addressed those forces? They include: | 1. Identifying the appropriate ESC Zone for aboveground structures (see ESC Zone) 2. Identifying corrosive factors of the submerged environment existing in soils, including resistivity, moisture, acidity, chlorides, sulfides, bacteria, differences in soil composition, and stray currents 3. Identifying the internal chemistry and corrosivity in pipes and conduits
4. Selecting appropriate materials 5. Preventing dissimilar metal corrosion 6. Using protective coatings, isolators, and corrosion inhibitors 7. Considering alternate materials for components near salt water and in areas of high environmental severity 8. Preventing intrusion of water and moisture
9. Consulting subject matter experts and stakeholders when appropriate 10. Providing close attention to construction practices that can increase corrosion risks, including field modifications, material substitutions, improper storage of materials, damage to coatings, field cuts, cut-edge corrosion, crevices, rough and sharp surfaces, poor coating selection and application, improper welding, improper installation of gaskets and other features that would allow leakage and infiltration into the structure (e.g., pipelines, valves, access manholes, cathodic protection [CP] features)
Buried metal pipelines and tanks usually suffer from corrosion because of one or more of the following soil conditions. Have these conditions been considered and addressed? | Low resistivity values; high moisture content; low pH values (acidity); presence of chlorides, sulfides, and bacteria; differences in soil composition
Has the environment been altered by: | Using a select backfill around a buried structure, using corrosion inhibitors, adjusting water chemistry in potable water systems, modifying structures to provide adequate drainage, using organic based deicers in lieu of chloride-based salts, relocating sources of stray currents
Corrosion rates can be greatly accelerated when two or more dissimilar metals are in contact with each other, particularly when they are buried or submerged. Have galvanic corrosion rates been effectively eliminated or minimized by: | Using as much of the same metal as possible, choosing metals close together in the galvanic series, placing a protective insulator between dissimilar metals, keeping the cathodic area small in relation to the anode area (for instance, bolts or screws of stainless steel for fastening aluminum sheets, but not the reverse, using special coatings on the metals), ensuring not to coat the anodes, providing CP if the structure is buried or immersed
Have the coating mechanisms for protection been considered? | 1. Barrier Protection – Protective coatings and linings attempt to isolate the structure from the environment (electrolyte); 2. Cathodic Protection – Some protective coatings have a high loading of fine zinc particles. Once cured, the electrical contact between the particles and underlying steel provide a type of CP; 3. Inhibitive Pigments – Some pigments are added to primers to inhibit corrosion at the coating/metal interface.
For internal corrosion of a pipe, the anode, cathode, and conductive material are all found in the pipe wall, while the electrolyte is the fluid transmitted within the pipe. Have the following key parameters affecting internal pipe corrosion for water distribution utilities been addressed? | Water quality and composition (pH, alkalinity, dissolved oxygen), ferric scale, flow conditions, biological activity, disinfectants, corrosion inhibitors |  |  | UFC 4-150-02 Dockside Utilities For Ship Service UFC 4-151-10 General Criteria For Waterfront Construction UFGS 33 30 00 Sanitary Sewers UFGS 33 11 00 Water Utility Distribution Piping UFGS 33 40 00 Storm Drainage Utilities UFGS 33 63 13 Exterior Underground Steam Distribution Systems
Have these factors been addressed? | For the majority of sanitary sewer systems, corrosion and rehabilitation are attributed to hydrogen-sulfide corrosion. Low velocity or stagnant conditions of the wastewater deplete dissolved oxygen, causing hydrogen-sulfide gas to be released into the air in the sewer pipe or structure. Specifically, bacteria convert sulfates in the sewage into sulfides, which make their way to the surface of the sewage and release into the sewer atmosphere as hydrogen sulfide (H2S) gas. Bacterial action on the top of the pipe or structure converts H2S gas to sulfuric acid, which causes corrosion in the crown of the pipe.
Steam Distribution Systems; Hot-Water Distribution Systems; Chilled Water & Condensed Water Distribution Systems
| Has corrosion been addressed in the design, construction and sustainment of distribution systems? |  |  | UFC 3-430-01FA Heating And Cooling Distribution Systems; UFC 3-430-02FA Central Steam Boiler Plants, UFC 3-430-07 Operations And Maintenance: Inspection And Certification Of Boilers And Unfired Pressure Vessels; UFC 3-430-08N Central Heating Plants; UFC 3-430-09 Exterior Mechanical Utility Distribution, AR 420-1 Facilities Engineering: Army Facilities Management
Are boilers, high-temperature/hot water (HTHW), and chilled water systems managed to avoid corrosion impacts?
Are distribution systems constructed to avoid corrosion impacts of design geometrics, for example, crevices that can trap water?
Wastewater Collection & Treatment (See Note 5 at the beginning of this Checklist (3) "Micro-environments")
| Have risks including highly corrosive environments, catastrophic equipment failure, rust, mildew, and CP-related corrosion risks been factored into the design, construction and sustainment? For clarification, mitigation actions include risks that CP can mitigate as well as these risks that CP can cause, such as over-applying CP, which can lead to coating disbondment and, in turn, wall corrosion. Each of these risks must be considered and addressed. |  |  | UFC 3-240-13FN Industrial Water Treatment Operation And Maintenance, AR 420-1 Facilities Engineering: Army Facilities Management
Have risks including water-borne corrosive pollutants, temperature, moisture, corrosive chemical reactions, abrasion, pitting, inadequate or malfunctioning CP, erosion, dissimilar metals, mold, mildew, and organic growth been factored into the design, construction and sustainment?
Have risks including public health risks, environmental pollution, and high costs of repairs and recovery been factored into the design, construction and sustainment? Do the plans for design, construction and sustainment make it clear that corrosion damage can lead to the aforementioned risks?
Industrial Water Treatment
| 1. Is there a water treatment program in place? |  |  | UFC 3-240-01 Wastewater Collection And Treatment; UFC 3-240-03 Operation And Maintenance (O&M): Wastewater Treatment ; UFC 3-240-13FN Industrial Water Treatment Operation and Maintenance; PWTB 420-49-5 Industrial Water Treatment Procedures; UFC 3-230-03 Water Treatment, AR 420-1, AFI 32-1054 Civil Engineer: Corrosion Control
| 2. Are control charts for each boiler, cooling tower and closed system developed and posted? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
| 3. Are the ion exchangers checked annually? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
| 4. Are condensate tests throughout the return system for possible water leakage at heat exchangers done at the start and end of heating season? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
| 5. When significant changes to IWT chemicals occur, are boiler total dissolved solid limits design acceptance tests and verification of the total protection of condensate return system done? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
| 6. Are IWT operating logs accomplished for each individual treated system? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control; AF IMT 1457 (Cooling Tower) and 1459 (Boilers); AF IMT 1457 (Cooling Tower) and 1459 (Boilers);
| 7. Are there historical records kept for each system? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
| 8. Are leaks from corrosion, tuberculation, and scaling in heating and cooling systems properly investigated and corrective action taken? |  |  | AFI 32-1054 Civil Engineer: Corrosion Control
Petroleum Oil Lubricants Storage Distribution Systems
| The system design, construction, and sustainment for POL distribution and storage is and must be a carefully managed DoD program. Record system failures (fuel leaks and monitoring) and explosions have ensured that appropriate attention be paid to this mission-critical area. Vigilance by planners, designers, engineers, SMEs, construction and sustainment personnel are required for system operation reliability. Have corrosion factors been addressed, per the specific line items below, to ensure structural integrity? |  |  | UFC 1-200-01 DoD Building Code (General Building Requirements); UFC 3-190-06 Protective Coatings and Paints; UFC 3-301-01 Structural Engineering; UFC 3-420-01 Plumbing Systems; UFC 3-430-09 Exterior Mechanical Utility Distribution; UFC 3-460-01 Design: Petroleum Fuel Facilities; UFC 3-460-03 O&M: Maintenance Of Petroleum Systems; UFC 3-501-01 Electrical Engineering; UFC 3-570-01 Cathodic Protection; UFC 3-570-06 O&M: Cathodic Protection Systems; UFC 3-575-01 Lightning and Static Electricity Protection Systems; UFC 3-600-01 Fire Protection Engineering for Facilities; UFC 3-810-01N Navy and Marine Corps Environmental Engineering for Facility Construction; UFC 4-141-10N Design: Aviation Operation and Support Facilities; UFC 4-150-02 Dockside Utilities for Ship Service; see also the Petroleum, Oil, And Lubricants (POL) Storage And Distribution Systems Knowledge Area on the CPC Source.
| Has planning, design, construction and sustainment programs addressed chloride containing environments, humidity, rain, salinity, structural loading, applied chemicals and contaminants, erosive forces, soil corrosivity, inadequate or malfunctioning Cathodic Protection (CP), internal corrosion (H2S, H2O, microbiologically induced corrosion), condensation, poor design geometrics and construction practices, dissimilar metal corrosion, and water entrapment and intrusion impacts on the system and individual facilities? |  |  | UFGS 02 65 00 Underground Storage Tank Removal; UFGS 09 90 00 Paints and Coatings; UFGS 09 96 00 High Performance Coatings; UFGS 09 97 02 Painting: Hydraulic Structures; UFGS 09 97 10.00 10 Metallic Coatings for Hydraulic Structures; UFGS 09 97 13.00 40 Steel Coatings; UFGS 09 97 13.15 Low VOC Polysulfide Interior Coating of Welded Steel Petroleum Fuel Tanks; UFGS 09 97 13.17 Three Coat Epoxy Interior Coating of Welded Steel Petroleum Fuel Tanks; UFGS 09 97 13.27 Exterior Coating of Steel Structures; UFGS 09 97 13.28 Protection of Buried Steel Piping and Steel Bulkhead Tie Rods; UFGS 09 97 23.13 Interior Lining for Concrete Storage Tanks (For Petroleum Fuels); UFGS 21 13 21.00 20 Foam Fire Extinguishing for Fuel Tank Protection; UFGS 26 42 13.00 20 Cathodic Protection by Galvanic Anodes; UFGS 26 42 14.00 10 Cathodic Protection System (Sacrificial Anode); UFGS 26 52 19.00 20 Cathodic Protection by Impressed Current UFGS 33 08 55 Commissioning of Fuel Facility Systems; UFGS 33 11 23 Natural Gas and Liquid Petroleum Piping
| Aboveground and buried POL distribution and storage facilities are essential for supplying fuel supplies to equipment, boilers, vehicles including back-up supplies for emergency generators. System failures in whole or in part can be hugely dangerous and disruptive to the mission and create environmental and health and safety concerns. POL system reliability is critically important. Have life-cycle decisions, including corrosion prevention and control, been made to ensure the reliability of POL Storage and distribution systems? |  |  | UFGS 33 51 15 Natural-Gas / Liquid Petroleum Gas Distribution; UFGS 33 52 10 Fuel Systems Piping (Service Station); UFGS 33 52 43.11 Aviation Fuel Mechanical Equipment; UFGS 33 52 43.13 Aviation Fuel Piping; UFGS 33 52 43.23 Aviation Fuel Pumps; UFGS 33 52 80 Liquid Fuels Pipeline Coating Systems; UFGS 33 56 10 Factory-Fabricated Fuel Storage Tanks; UFGS 33 58 00 Leak Detection for Fueling Systems; UFGS 33 61 13.19 Valves, Piping, and Equipment In Valve Manholes; UFGS 40 05 13 Pipelines, Liquid Process Piping; UFGS 41 65 10.00 10 [Diesel][Natural Gas] Fueled Engine Pump Drives
Are the following best practices being applied: 1. Maintaining and conducting an active preventative maintenance program to include inspections that focus on CPC. 2. Maintaining and inspecting CP systems. 3. Incorporating good Design Geometrics. 4. Maintaining and applying an awareness and application of ESC Zone requirements and impacts. 5. Ensuring that the design component or assembly complies with the requirements from the RFP, including performance technical specifications, referenced UFC and UFGS documents. 6. Ensuring that the design drawings and specifications address CPC through proper choice of materials and coatings. 7. Selecting and specifying materials and coatings that have low life cycle costs, are durable, and minimize the need for preventative and corrective maintenance. Initial investments in corrosion prevention are typically more life—cycle cost effective than maintenance, repair, and replacement of prematurely degraded components. 8. Designing and specifying POL storage and distribution systems to reach the intended service life, including the use of enhanced materials, coatings, and appropriate application of CP as defined in UFC and UFGS criteria in severe corrosive environments. 9. Leveraging the insights provided in the Corrosion Prevention and Control Checklists Tool
Fences & Gates
| When material selection is inconsistent with the ESC Zone designations in UFC 1-200-01, system performance impacts security and life cycle; corrosion-caused appearance degradation can be visible very quickly; sustainment costs can be significant. Have these risks been addressed and factored into the design, construction and sustainment? |  |  | UFC 1-300-02 UFGS Format Standard, UFC 3-220-10N Soil Mechanics, UFC 3-701-01 DoD Facilities Pricing Guide, UFC 4-010-01 DoD Minimum Antiterrorism Standards for Buildings, UFC 4-010-03 Security Engineering: Physical Security Measures for High-Risk Personnel, UFC 4-020-01 DoD Security Engineering Planning Manual, UFC 4-022-02 Selection and Application of Vehicle Barriers, UFC 4-022-03 Security Fences and Gates, UFC 4-141-10N Design, Aviation Operation and Support Facilities, UFGS 32 31 13 Chain Link Fences and Gates, UFGS 32 31 13.53 High-Security Chain Link Fences and Gates, UFGS 32 31 26 Wire Fences and Gates; see the Corrosion Prevention & Control (CPC) Fencing Knowledge Area for additional information.
Chloride-containing environments, humidity, rain, dissimilar metals causing galvanic corrosion, water entrapment, highly corrosive soils, salinity, structural loading, airborne chemicals and contaminants, erosive forces, and condensation affect fencing facility performance. Have these risks been factored into the design, construction and sustainment?
Operational readiness is reduced when physical security risks occur. Appearance degradation and reduction in access-denial requirements also harm operational readiness. Have these risks been factored into the design, construction and sustainment? Have plans for design, construction, and sustainment made it clear that corrosion damage can increase operational risks?
Have the following factors affecting fencing design and durability been considered: | 1. Function: Security, safety, entry requirements, and boundary identification; 2. Environmental severity and location specific corrosivity; 3. Structural integrity of posts, fabric, supporting members, and gates; 4. Aesthetics: Does fencing comply with an installation's appearance plan, if there is one?
| UFC 4-022-03 requires that “design strategies for installation security structures and equipment must consider corrosion prevention and control (CPC) preservation techniques for long-term maintainability throughout their life cycle. Trade-off decisions involving cost, useful service life, and effectiveness must address corrosion prevention and mitigation.” |  |  | UFC 4-022-03 Security Fences and Gates
| In the area of Material Selection and Coatings, “Local environments must be considered during the selection of material for the fencing components as well as the required coatings to provide protection against corrosion. Color polymer and other coatings on fencing fabric, fittings, framework, and gates must be applied to enhance visibility and provide greater corrosion resistance, especially in corrosive or salt laden environment.” |  |  | UFC 4-022-03 Security Fences and Gates
| “Coating on any fasteners or ties must be electrolytically compatible with fencing fabric to inhibit corrosion. All security fence fittings must be electrolytically compatible with all fence components. One of the most important corrosion issues is the chemical reaction between dissimilar metals. When dissimilar metals are in contact with one another in the presence of an electrolyte, galvanic action occurs, resulting in their deterioration. The electrolyte may be rain water running from one surface to another, or moisture from the air containing enough acid to cause it to act as an electrolyte.” |  |  | UFC 4-022-03 Security Fences and Gates
From an Operations and Maintenance (O&M) perspective, the constructed facility that provides the least effort to maintain and meets performance, security, and appearance objectives is preferable. In more severe environments, fencing materials and coatings with better corrosion resistance can reduce O&M costs. Often, corrosion-damaged fencing is replaced with the same materials, adding to a negative life-cycle impact
| Ideally, all components of the fencing system should address corrosion vulnerability and durability. According to the findings in the Project Report for F09-AR02, “results indicate that using corrosion-resistant materials could reduce the life-cycle costs of fences and railings by 62 to 80%. The return on investment (ROI) ratio for using fuse-bonded fencing and anodized aluminum railings was calculated at 6.13; and the ROI for using FRP composite railings instead of anodized aluminum was 5.75.” |  |  | F09-AR02 (Construction Engineering Research Laboratory (CERL), U.S. Army Corps of Engineers (USACE) Engineer Research and Development Center (ERDC) Project F09-AR02 Final Report, Demonstration and Validation of Materials for Corrosion-Resistant Fencing and Guard Railings in Aggressive Climates (October 2015)
Have the following factors affecting fencing design and durability been considered? | 1. Selection of materials to prevent dissimilar metal corrosion 2. Use of protective coatings, isolators, and corrosion inhibitors 3. Consideration of alternate materials for components proximate to salt water and in areas of high environmental severity 4. Prevention of entrapment of water 5. Provision of appropriate grounding features (see UFC 4-022-03) 6. Reinforcement for the fencing structure
MDACS requires the following: | "Perimeter fences shall be aluminized (aluminum coated steel) fencing components, including fence fabric in accordance with ASTM A-491, post, rails, braces and gates in accordance with ASTM B211-03 and verified by the [Contracting Officer’s Representative] COR for appropriate locations. Polyvinyl chloride (PVC) coatings shall be in color and a minimum thickness of 2 mm (0.10 inches). Verify if top and/or bottom tension wires and top and/or bottom rails are to be provided; where tying into an existing fence, match the fencing system." |  |  | Marianas Navy and Marine Corps Design and Construction Standards (MDACS) (September 2017); See UFC 1-200-01.
MDACS requires the following: | "Provide an ornamental or decorative fence of aluminized (aluminum coated) steel with a colored vinyl or other approved coating for recreational or housing fences as verified and approved by the COR. Polyvinyl chloride (PVC) coatings shall be in color and a minimum thickness of 2 mm (0.10 inches). An optional decorative fence type is hot-dipped galvanized steel with a colored vinyl coating, which shall be verified with the COR." |  |  | Marianas Navy and Marine Corps Design and Construction Standards (MDACS) (September 2017); See UFC 1-200-01.
MDACS requires the following: | "Perimeter and security fences shall conform to the applicable base installation appearance plan as appropriate and be reviewed by the [Public Affairs Officer] PAO or Base Security officer." |  |  | Marianas Navy and Marine Corps Design and Construction Standards (MDACS) (September 2017); See UFC 1-200-01.
In the category of Best Practices, has the design, construction, and sustainment considered: | Materials and systems used in fencing have to adhere to certain minimum industry exposure testing standards, such as moisture, UV, and salt spray testing (ASTM G152-ASTM G155). |  |  | ASTM G152-ASTM G155
Fence posts are normally encased in concrete and are not in direct ground contact. In high-corrosivity soils, there are concrete mix options to reduce concrete permeability.
Post caps get knocked off, allowing rain to fall inside the post where it becomes trapped, causing internal corrosion, weakening the fence post.
Fence fabric is usually the first component to degrade and need maintenance or replacement.
Typically, a zinc coating (galvanizing) is used, unless there is a specific requirement like the use of PVC in high-visibility areas or for highly corrosive environments.

## Facility Assessment Checklist
Facility Assessment Checklist (Developed by Steve Geusic, P.E.)
Evaluation Date
Building Location
Building Number
Inspector
Signature/Date
Reason For Evaluation
Building POC
Current Weather Conditions, Temperature, & humidity level:
CASTROPHIC EVENT
Y/N |  | COMMENT
Hurricane or Storm - Name:_______________ Date:___________
Wind damage (describe breach in building envelope)
Flood: Date_______________
High water mark above exterior grade____________________ft.
High water mark interior above finish floor_________________ft.
Is site still flooded? Depth of water (exterior)_______________ft.
Discharge of water from building system :____________________
EXTERIOR SITE AND BUILDING VISUAL REVIEW
Y/N |  | COMMENT
Sources of outside molds and organics (for example, leaf piles and mulch)
Organic or pathogenic (bird droppings) material in or near air intakes
Poor drainage (grading)
Standing water where it may be affecting the indoor environment
Damage to the building foundation or walls
Cracking/Peeling/Rotting building finish
Problems with window and door fit or caulking
Roofing problems (membrane, flashing, penetrations, drains)
Moisture problems within foundation crawlspace/basement
Other Specify
Moisture Reading Level (include location & type of material)
INTERVIEW WITH OCCUPANTS AND MAINTENANCE STAFF (POC):
Y/N |  | COMMENT
Has building been recently renovated or repaired?
Are building occupants reporting poor indoor air quality or odors?
Are building occupants reporting any sensitivity to air quality?
History of moisture or leaks?
Other: Specify
HEATING, VENTILATION, AND AIR-CONDITIONING (HVAC) SYSTEM VISUAL REVIEW
Y/N |  | COMMENT
Filters (dampness and microbial growth, dirt)
Heat exchangers (e.g., cooling coil section including drain pan)
Ductwork (for dampness, microbial growth, dirt, and rust)
Air diffusers/Vents (for dampness, microbial growth, dirt, rust)
INTERIOR SPACE REVIEW: GENERAL EVALUATION
Y/N |  | COMMENT
Odors and indoor air quality issues
Inappropriate temperature or humidity level
Moisture Reading Level (include location & type of material)
Cleanliness issues, dust, or unsanitary conditions
Evidence of roaches, flies, mice, rats, etc.
Presence of chemicals, solvents, or pesticides
Visible leaks
Odors and air quality issues from adjacent areas (adjacent area use)
Other specify
INTERIOR SPACE REVIEW: MOISTURE AND MOLD: (Provide digital photograph of areas of suspected mold)
*Moisture present or visible damage/discoloration from water.
Surfaces, systems, and building components |  | Water Y/N | Mold Y/N | Photo ID | Comments: (Note material type, location on material, and if contaminated surface is porous or non-porous)
Flooring (carpet, padding, vinyl, tile, wood, raised flooring)
Walls and molding (include type of substrate and covering; describe condition, bubbling, peeling, discolored)
Windows and doors (surface condensation, water leaks, and air leaks)
Ceiling, lighting, and skylights
Ceiling cavity above drop ceiling (ductwork and piping)
HVAC registers (identify location) (dampness, microbial growth, rust, and dirt)
Portable humidifiers (for standing water, microbial growth, and dirt)
Room air conditioners and filters (standing water, microbial growth, dirt)
Radiators, chill beams, and other direct heating sources
Furniture, window treatments, shelving, appliances, storage containers (for dampness, microbial growth, and dirt)
Around and on plumbing fixtures, laundry and kitchen equipment.
Closets or utility area
Hidden area inspection (wall cavity-camera)
Other specify